## TITLE PAGE
Water Resources Planning Tables 2019
v15 - June 2018
All queries on the content of this workbook should be sent to:
water-company-plan@environment-agency.gov.uk
Water resource zone information
Company: |  | Portsmouth Water
Resource Zone Name: |  | Company |  |  |  |  | Data validation: Cell D20
Resource Zone Number: |  | PRT 1 |  |  |  |  | Dry Year Annual Average
Planning Scenario Name: |  | Dry Year Annual Average - benchmarking data | 0 | 0 |  |  | Dry Year Critical Period
Chosen Level of Service: |  | 1 in 200 |  |  |  |  | Dry Year Annual Average - benchmarking data
Base Year: |  | 2017/18 |  |  |  |  | Dry Year Critical Period - benchmarking data
Responsible Officer: |  | Steve Morley | Signed: |  | Dated: | 6.9.18
Version: |  | Draft Final Plan |  | [Digital signature is acceptable]
Key to cells
Clear cells - indicate an input is required
Yellow shaded cells - indicates a formula.
Blue shaded cells - indicate base year data.
Light grey shaded cells - indicate preceding years.
Dark grey cells - indicate that no data entry is required.
Worksheet |  | Content
WRZ summary |  | Supply-Demand Balance and components
1. BL Licences |  | Baseline water resources
2. BL Supply |  | Baseline water supplies
3. BL Demand |  | Baseline demand
4. BL SDB |  | Baseline supply demand balance
5. Feasible options |  | Fixed and Variable costs, Net Present Value, AIC and AISC of all feasible options (confidential)
6. Preferred options |  | High level costs of preferred options (Dry Year) - publicly available
7. FP Supply |  | Final Planning water supplies (impact of Scenario options)
8. FP Demand |  | Final Planning demand (impact of Scenario options)
9. FP SDB |  | Final Planning supply demand balance
10. Drought plan links |  | Drought plan links

## WRZ summary
Summary graphs of water resources planning tables data
Portsmouth Water
Company
DERIVATION | DESCRIPTION | UNITS |  | For info 2017-18 | For info 2018-19 | For info 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-2030 | 2030-2031 | 2031-2032 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
SUPPLY
13BL | Total water available for use | Ml/d | 160.34 | 160.34 | 160.34 | 152.68 | 145.1445 | 145.109 | 145.0735 | 144.588 | 135.5525 | 135.517 | 135.4815 | 135.446 | 135.4105 | 113.235 | 113.1995 | 113.164 | 113.1285 | 113.093 | 113.0575 | 113.022 | 112.9865 | 112.951 | 112.9155 | 112.88 | 112.8445 | 112.809 | 112.7735 | 112.738 | 112.7025
13FP | Total water available for use | Ml/d | 168.84 | 168.84 | 168.84 | 168.98 | 161.4445 | 161.409 | 161.3735 | 160.888 | 164.3525 | 164.317 | 164.2815 | 164.246 | 164.2105 | 165.035 | 164.9995 | 164.964 | 164.9285 | 164.893 | 164.8575 | 164.822 | 164.7865 | 164.751 | 164.7155 | 164.68 | 164.6445 | 164.609 | 164.5735 | 164.538 | 164.5025
| DEMAND |  | 1.578
26BL | Unmeasured household consumption | Ml/d | 79.06 | 79.06 | 78.09 | 77.33 | 76.54 | 75.8 | 75.1 | 74.43 | 73.8 | 73.2 | 72.62 | 72.1 | 71.61 | 71.14 | 70.7 | 70.29 | 69.9 | 69.53 | 69.18 | 68.84 | 68.53 | 68.22 | 67.93 | 67.65 | 67.39 | 67.13 | 66.89 | 66.65 | 66.43
26FP | Unmeasured household consumption | Ml/d | 68.82 | 68.82 | 67.99 | 67.3617 | 65.2192 | 63.2271 | 61.2126 | 59.2188 | 56.9495 | 52.8471 | 49.1344 | 45.6802 | 42.4747 | 39.468 | 36.6704 | 34.0817 | 31.6823 | 29.442 | 27.3809 | 25.4392 | 23.6168 | 21.9538 | 20.4002 | 18.9461 | 17.6115 | 16.3665 | 15.2011 | 14.0953 | 13.1026
25BL | Measured household consumption | Ml/d | 23.06 | 23.06 | 24.74 | 26.48 | 28.09 | 29.56 | 30.93 | 32.23 | 33.45 | 34.61 | 35.67 | 36.62 | 37.52 | 38.38 | 39.2 | 40.01 | 40.83 | 41.64 | 42.41 | 43.18 | 43.93 | 44.68 | 45.41 | 46.13 | 46.85 | 47.55 | 48.23 | 48.92 | 49.59
25FP | Measured household consumption | Ml/d | 20.74 | 20.74 | 22.28 | 23.89 | 25.9946 | 28.0883 | 30.0412 | 31.9702 | 33.6292 | 37.7482 | 41.4459 | 44.7739 | 47.8621 | 50.7705 | 53.4591 | 56.0079 | 58.4567 | 60.7358 | 62.8749 | 64.9142 | 66.8335 | 68.673 | 70.3825 | 72.0122 | 73.5719 | 75.0617 | 76.4415 | 77.7914 | 79.0714
23BL+24BL | Non-household consumption | Ml/d | 34.05 | 34.05 | 33.89 | 33.7 | 33.52 | 33.34 | 33.16 | 32.97 | 32.8 | 32.61 | 32.42 | 32.24 | 32.05 | 31.87 | 31.68 | 31.5 | 31.31 | 31.12 | 30.93 | 30.75 | 30.58 | 30.44 | 30.29 | 30.15 | 30.01 | 29.86 | 29.72 | 29.57 | 29.43
23FP+24FP | Non-household consumption | Ml/d | 25.95 | 25.95 | 25.79 | 25.6 | 25.42 | 25.24 | 25.06 | 24.87 | 24.7 | 24.51 | 24.32 | 24.14 | 23.95 | 23.77 | 23.58 | 23.4 | 23.21 | 23.02 | 22.83 | 22.65 | 22.48 | 22.34 | 22.19 | 22.05 | 21.91 | 21.76 | 21.62 | 21.47 | 21.33
40BL | Total leakage | Ml/d | 35.04 | 35.04 | 34.95 | 34.89 | 34.9 | 34.93 | 34.99 | 35.05 | 35.11 | 35.17 | 35.24 | 35.37 | 35.49 | 35.61 | 35.73 | 35.82 | 35.92 | 36.01 | 36.1 | 36.17 | 36.25 | 36.33 | 36.4 | 36.46 | 36.51 | 36.58 | 36.64 | 36.7 | 36.75
40FP | Total leakage | Ml/d | 35.04 | 35.04 | 34.95 | 34.87 | 33.5 | 32.1 | 30.7 | 29.3 | 27.9 | 27.64 | 27.38 | 27.12 | 26.86 | 26.6 | 26.34 | 26.08 | 25.82 | 25.56 | 25.3 | 25.04 | 24.78 | 24.52 | 24.26 | 24 | 23.74 | 23.48 | 23.22 | 22.96 | 22.7
11BL-(23BL:26BL)-40BL | Other components of demand | Ml/d | 2.88 | 2.88 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 2.8789
11FP-(23FP:26FP)-40FP | Other components of demand | Ml/d | 2.88 | 2.88 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 2.8789 | 2.8789
| Total demand + target headroom (baseline) | Ml/d | 179.35 | 179.35 | 179.8089 | 180.5889 | 181.2689 | 181.6089 | 182.2689 | 182.9089 | 183.6389 | 183.4589 | 184.1189 | 184.7889 | 185.6389 | 185.6689 | 185.3289 | 186.1889 | 186.9389 | 187.6089 | 188.0789 | 187.8389 | 188.9689 | 189.5789 | 190.1589 | 190.6489 | 190.4589 | 190.9389 | 191.6189 | 192.1389 | 192.6589
| Total demand + target headroom (final plan) | Ml/d | 158.69 | 158.69 | 159.1489 | 159.9106 | 158.3528 | 156.6343 | 155.1027 | 153.5879 | 151.6576 | 150.6142 | 150.4493 | 150.173 | 150.1157 | 149.2775 | 148.0684 | 148.1385 | 148.1479 | 148.0667 | 147.8448 | 146.9422 | 147.3892 | 147.3957 | 147.3616 | 147.2672 | 146.5323 | 146.4871 | 146.6215 | 146.6156 | 146.6628
SUPPLY-DEMAND BALANCE
16BL | Target headroom | Ml/d | 5.26 | 5.26 | 5.26 | 5.31 | 5.34 | 5.1 | 5.21 | 5.35 | 5.6 | 4.99 | 5.29 | 5.58 | 6.09 | 5.79 | 5.14 | 5.69 | 6.1 | 6.43 | 6.58 | 6.02 | 6.8 | 7.03 | 7.25 | 7.38 | 6.82 | 6.94 | 7.26 | 7.42 | 7.58
16FP | Target headroom | Ml/d | 5.26 | 5.26 | 5.26 | 5.31 | 5.34 | 5.1 | 5.21 | 5.35 | 5.6 | 4.99 | 5.29 | 5.58 | 6.09 | 5.79 | 5.14 | 5.69 | 6.1 | 6.43 | 6.58 | 6.02 | 6.8 | 7.03 | 7.25 | 7.38 | 6.82 | 6.94 | 7.26 | 7.42 | 7.58
17BL | Available headroom | Ml/d | -13.75 | -13.75 | -14.2089 | -22.5989 | -30.7844 | -31.3999 | -31.9854 | -32.9709 | -42.4864 | -42.9519 | -43.3474 | -43.7629 | -44.1384 | -66.6439 | -66.9894 | -67.3349 | -67.7104 | -68.0859 | -68.4414 | -68.7969 | -69.1824 | -69.5979 | -69.9934 | -70.3889 | -70.7944 | -71.1899 | -71.5854 | -71.9809 | -72.3764
17FP | Available headroom | Ml/d | 15.41 | 15.41 | 14.9511 | 14.3794 | 8.4317 | 9.8747 | 11.4808 | 12.6501 | 18.2949 | 18.6928 | 19.1222 | 19.653 | 20.1848 | 21.5475 | 22.0711 | 22.5155 | 22.8806 | 23.2563 | 23.5927 | 23.8998 | 24.1973 | 24.3853 | 24.6039 | 24.7928 | 24.9322 | 25.0619 | 25.212 | 25.3424 | 25.4197
Baseline Supply-Demand Balance:
|  | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-2030 | 2030-2031 | 2031-2032 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
| SDB (Ml/d) | -36.1244 | -36.4999 | -37.1954 | -38.3209 | -48.0864 | -47.9419 | -48.6374 | -49.3429 | -50.2284 | -72.4339 | -72.1294 | -73.0249 | -73.8104 | -74.5159 | -75.0214 | -74.8169 | -75.9824 | -76.6279 | -77.2434 | -77.7689 | -77.6144 | -78.1299 | -78.8454 | -79.4009 | -79.9564
Final Planning Supply-Demand Balance:
|  | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-2030 | 2030-2031 | 2031-2032 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
| SDB (Ml/d) | 3.0917 | 4.7747 | 6.2708 | 7.3001 | 12.6949 | 13.7028 | 13.8322 | 14.073 | 14.0948 | 15.7575 | 16.9311 | 16.8255 | 16.7806 | 16.8263 | 17.0127 | 17.8798 | 17.3973 | 17.3553 | 17.3539 | 17.4128 | 18.1122 | 18.1219 | 17.952 | 17.9224 | 17.8397
| Company: | [6 empty] | Portsmouth Water
| Resource Zone Name | [6 empty] | Company
| Resource Zone Number: | [6 empty] | PRT 1
| Planning Scenario Name: | [6 empty] | Dry Year Annual Average - benchmarking data
| Chosen Level of Service: | [6 empty] | 1 in 200

## 1. BL Licences
Table 1: Baseline licences |  |  |  |  | deployable output (Ml/d)
Row ref | Derivation | Licence number | Source name | Source type | Deployable output (Ml/d) | Annual licensed quantity (Ml/d) | Constraints on deployable output | Additional notes (if desired)
All individual licences: |  |  |  |  | 190.7 | 311.63
0.1BL | Sum (0.1BL+...) | - | - | - | 114.7 | 218.21 | -
| Input |  | Source A | SW:River | 20 | 45.5 | Licence | Licence varied 2011 MRF set
| Input |  | Source C | GW | 16.3 | 20.51 | Licence | Turbidity issues
| Input |  | Source D | GW | 0.8 | 0 | Pump level | Linked to Source C
| Input |  | Source E | GW | 0.4 | 0.46 | Licence | Standby source
| Input |  | Source F | GW | 6.9 | 9.02 | Licence | Licence varied 2015 Augmentation
| Input |  | Source G | GW | 1.5 | 0 | Licence | Linked to Source S
| Input |  | Source H | GW | 7.2 | 9.12 | Licence | Flow condition
| Input |  | Source I | GW | 1.4 | 1.5 | Flow condition | Licence varied 2015 MRF set
| Input |  | Source J | GW | 8.3 | 22.73 | DAPWL | Water quality issues
| Input |  | Source K | GW | 9 | 11.37 | Licence | Water quality issues
| Input |  | Source B | GW | 42.9 | 98 | Flow condition | Licence varied 2009 MRF set
Input
Grouped licences | Derivation | Licence number | Source name | Source type | DYAA deployable output (Ml/d) | Annual licensed quantity (Ml/d)
0.2BL | Sum (0.2BL+...) | - | Total | - | 76 | - | -
- | - | Group #: | [Enter name of group] | - | 76 | - | -
| Input |  | Sources L-P | GW | 48 | 65.04 | Licence | River Ems augmentation
| Input |  | Sources Q-T | GW | 28 | 28.38 | Pump capacity | Nitrate blending/Bulk supply
- | Input
Unused licences: | Derivation | Licence number | Source name | Source type | DYAA deployable output (Ml/d) | Annual licensed quantity (Ml/d) | Reason licence is unused
0.3BL | Sum (0.3BL+...) | - | - | - | 0 | 3.02 | -
| Input |  | Source U | GW | 0 | 3.02 | Emergency use only | Raw water augmentation R Ems
- | Input
New licences (within current AMP): | Derivation | Licence number | Source name | Source type | DYAA deployable output (Ml/d) | Annual licensed quantity (Ml/d) | Status of licence
0.4BL | Sum (0.4BL+...) | - | - | - | 0 | 0 | -
Input
- | Input
- | - | - | - | - | - | - | -
Company: |  | Portsmouth Water
Resource Zone Name: |  | Company
Resource Zone Number: |  | PRT 1
Planning Scenario Name: |  | Dry Year Annual Average - benchmarking data
Chosen Level of Service: |  | 1 in 200
README
Note on C3: Please list only individual licences (i.e. not used in conjunctive use systems).
Note on B19: If additional lines are required please insert into middle of group to ensure automatic calculations pick up all data.
Note on B26: If additional lines are required please insert into middle of group to ensure automatic calculations pick up all data. DO NOT DELETE DEFAULT INPUT ROWS - If unrequired leave blank.
Note on J27: Please state if a licence has been applied for, approved, granted, awaiting mobilisation, or other specified status.
Note on C39: Do not delete default inserted input lines. These are required to generate the autosum of all additional rows added. Additional rows which the user enters can be deleted.

## 2. BL Supply
Table 2: Baseline supply
| Row ref | Component | Derivation | Unit | decimal places | 2017/18 | For info 2017-18 | For info 2018-19 | For info 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-2030 | 2030-2031 | 2031-2032 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
| 1BL | Raw water abstracted | Input | Ml/d | 2
Resources | 2BL | Total raw water imported | sum(2.1BL+2.2BL+2.3BL...) | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2.1BL+ | Raw water imported from: None | Input | Ml/d | 2
| - | - | - | - | 2 |  | - | - | - |  | - | - | - | - | - | - | - | - | - | - | - | bar: 2032-33 to 2044-45
| 3BL | Total potable water imported | sum(3.1BL+3.2BL+3.3BL...) | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 3.1BL+ | Potable water imported from: None | Input | Ml/d | 2
| - | - | - | - | 2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: 2032-33 to 2044-45
| 5BL | Total raw water exported (raw exports and non potable uses) | sum(5.1BL+5.2BL+...) | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 5.1BL | Non potable water supplied to: | Input | Ml/d | 2
| 5.2BL+ | Raw water export to: None | Input | Ml/d | 2
| - |  | - | - | 2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: 2032-33 to 2044-45
| 6BL | Total potable water exported | sum(6.1BL+6.2BL+6.3BL...) | Ml/d | 2 | 15 | 15 | 15 | 22.5 | 30 | 30 | 30 | 30 | 39 | 39 | 39 | 39 | 39 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
| 6.1BL+ | Potable water export to Sussex North | Input | Ml/d | 2 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
| 6.2BL+ | Potable water export to Hants South Phase 1 | Input | Ml/d | 2 | 0 | 0 | 0 | 7.5 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
| 6.3BL | Potable water export to Hants South Phase 2 | Input | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
| 6.4BL | Potable water export to Hants South Phase 3 | Input | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21 | 21
| 7BL | Deployable Output (baseline profile without reductions) | sum(0.1Bl+0.2BL+0.3BL+0.4BL) | Ml/d | 2 | 190.7 | 190.7 | 190.7 | 190.7 | 190.7 | 190.7 | 190.7 | 190.7 | 190.7 | 190.7 | 190.7 | 190.7 | 190.7 | 190.7 | 190.7 | 190.7 | 190.7 | 190.7 | 190.7 | 190.7 | 190.7 | 190.7 | 190.7 | 190.7 | 190.7 | 190.7 | 190.7 | 190.7 | 190.7
Resource (and process) Losses | 8BL | Baseline forecast changes to Deployable Output | sum(8.1BL+8.2BL+8.3BL) | Ml/d | 2 | 0 | 0 | 0 | -0.07 | -0.1055 | -0.141 | -0.1765 | -0.212 | -0.2475 | -0.283 | -0.3185 | -0.354 | -0.3895 | -0.425 | -0.4605 | -0.496 | -0.5315 | -0.567 | -0.6025 | -0.638 | -0.6735 | -0.709 | -0.7445 | -0.78 | -0.8155 | -0.851 | -0.8865 | -0.922 | -0.9575
| 8.1BL | Change in DO due to climate change | Input (reductions must be expressed as -ve) | Ml/d | 2 | 0 | 0 | 0 | -0.07 | -0.1055 | -0.141 | -0.1765 | -0.212 | -0.2475 | -0.283 | -0.3185 | -0.354 | -0.3895 | -0.425 | -0.4605 | -0.496 | -0.5315 | -0.567 | -0.6025 | -0.638 | -0.6735 | -0.709 | -0.7445 | -0.78 | -0.8155 | -0.851 | -0.8865 | -0.922 | -0.9575
| 8.2BL | Reductions to restore sustainable abstraction | sum(8.2BL sub components) | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 8.2BL+ | Total for the zone | Input (zero or negative number) | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| - |  | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: 2032-33 to 2044-45
| 8.3BL | Total other changes to DO (specify, e.g. nitrates): None | Input (reductions must be expressed as -ve) | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| - |  | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: 2032-33 to 2044-45
| 9BL | Raw water losses, treatment works losses and operational use | Input | Ml/d | 2 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4
| 10BL | Outage allowance | Input | Ml/d | 2 | 12.96 | 12.96 | 12.96 | 13.05 | 13.05 | 13.05 | 13.05 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 14.64 | 14.64 | 14.64 | 14.64 | 14.64 | 14.64 | 14.64 | 14.64 | 14.64 | 14.64 | 14.64 | 14.64 | 14.64 | 14.64 | 14.64 | 14.64
|  | Company: | Portsmouth Water
|  | Resource Zone Name: | Company
|  | Resource Zone Number: | PRT 1
|  | Planning Scenario Name: | Dry Year Annual Average - benchmarking data
|  | Chosen Level of Service: | 1 in 200
Note on D15: Author: 08/04/2019: Updated to 15 Ml/d in all years
Note on D16: Author: 08/04/2019: Changed to 7.5Ml/d in 2019/20 due to SRN network contraints
Note on D28: Author: 08/04/2019: Outage Allowance reduced bp 1.7 Ml/d reflecting the removal of planned outage 24/05/2019: Updated in line with revised 2019 reassessment

## 3. BL Demand
Table 3: Baseline demand
| Row ref | Component | Derivation | Unit | Decimal places | 2017/18 | For info 2017-18 | For info 2018-19 | For info 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-2030 | 2030-2031 | 2031-2032 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
Consumption | 19BL | Water delivered measured non-household | Input | Ml/d | 2 | 33.48 | 33.48 | 33.31 | 33.12 | 32.93 | 32.74 | 32.55 | 32.36 | 32.18 | 31.99 | 31.8 | 31.61 | 31.42 | 31.24 | 31.05 | 30.86 | 30.67 | 30.48 | 30.29 | 30.1 | 29.93 | 29.79 | 29.64 | 29.5 | 29.35 | 29.2 | 29.06 | 28.91 | 28.77
| 20BL | Water delivered unmeasured non- household | Input | Ml/d | 2 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
| 21BL | Water delivered measured household | Input | Ml/d | 2 | 24.85 | 24.85 | 26.53 | 28.27 | 29.93 | 31.46 | 32.92 | 34.3 | 35.6 | 36.84 | 37.98 | 39.08 | 40.12 | 41.11 | 42.06 | 42.98 | 43.91 | 44.82 | 45.69 | 46.55 | 47.39 | 48.22 | 49.03 | 49.82 | 50.61 | 51.38 | 52.13 | 52.88 | 53.61
| 22BL | Water delivered unmeasured household | Input | Ml/d | 2 | 85.18 | 85.18 | 84.19 | 83.41 | 82.6 | 81.84 | 81.12 | 80.43 | 79.79 | 79.17 | 78.58 | 78.05 | 77.54 | 77.06 | 76.61 | 76.19 | 75.79 | 75.41 | 75.05 | 74.7 | 74.38 | 74.07 | 73.77 | 73.48 | 73.21 | 72.95 | 72.7 | 72.46 | 72.23
| 23BL | Measured Non Household - Consumption | 19BL-34BL | Ml/d | 2 | 33.2 | 33.2 | 33.03 | 32.84 | 32.66 | 32.47 | 32.29 | 32.1 | 31.93 | 31.74 | 31.55 | 31.37 | 31.18 | 31 | 30.81 | 30.63 | 30.44 | 30.25 | 30.06 | 29.88 | 29.71 | 29.57 | 29.42 | 29.28 | 29.14 | 28.99 | 28.85 | 28.7 | 28.56
| 24BL | Unmeasured Non Household - Consumption | 20BL-35BL | Ml/d | 2 | 0.85 | 0.85 | 0.86 | 0.86 | 0.86 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87
| 25BL | Measured Household - Consumption | 21BL-36BL | Ml/d | 2 | 23.06 | 23.06 | 24.74 | 26.48 | 28.09 | 29.56 | 30.93 | 32.23 | 33.45 | 34.61 | 35.67 | 36.62 | 37.52 | 38.38 | 39.2 | 40.01 | 40.83 | 41.64 | 42.41 | 43.18 | 43.93 | 44.68 | 45.41 | 46.13 | 46.85 | 47.55 | 48.23 | 48.92 | 49.59
| 26BL | Unmeasured Household - Consumption | 22BL-37BL | Ml/d | 2 | 79.06 | 79.06 | 78.09 | 77.33 | 76.54 | 75.8 | 75.1 | 74.43 | 73.8 | 73.2 | 72.62 | 72.1 | 71.61 | 71.14 | 70.7 | 70.29 | 69.9 | 69.53 | 69.18 | 68.84 | 68.53 | 68.22 | 67.93 | 67.65 | 67.39 | 67.13 | 66.89 | 66.65 | 66.43
| 27 - | Percentage of consumption driven by climate change | Input | % | 1 | 0% | 0% | 2% | 4% | 5% | 7% | 9% | 11% | 13% | 15% | 16% | 18% | 20% | 22% | 24% | 25% | 27% | 29% | 31% | 33% | 35% | 36% | 38% | 40% | 42% | 44% | 45% | 47% | 49%
| 28 - | Volume of consumption driven by climate change |  | Ml/d | 1 | 0 | 0 | 0.027344 | 0.055004 | 0.069075 | 0.09709 | 0.12527 | 0.15359 | 0.18207 | 0.21063 | 0.22514 | 0.25373 | 0.28236 | 0.31106 | 0.33979 | 0.3545 | 0.38351 | 0.41264 | 0.44181 | 0.47114 | 0.50064 | 0.51602 | 0.54579 | 0.57572 | 0.60585 | 0.63598 | 0.65178 | 0.68216 | 0.71271
PCC and consumption by component | 29BL | Measured Household - PCC | (25BL*1,000,000)/(51BL*1,000) | l/h/d | 1 | 133.5 | 133.5 | 133.5 | 133.8 | 133.8 | 133.8 | 133.6 | 133.4 | 133.2 | 133.1 | 132.9 | 132.6 | 132.3 | 132.1 | 131.9 | 131.8 | 131.7 | 131.7 | 131.7 | 131.7 | 131.7 | 131.7 | 131.8 | 131.8 | 131.9 | 131.9 | 131.9 | 132 | 132
| 29.1BL | Measured toilet flushing | Input | l/h/d | 1 | 32.9 | 32.9 | 32.9 | 32.8 | 32.6 | 32.4 | 32.1 | 31.9 | 31.6 | 31.4 | 31.1 | 30.9 | 30.6 | 30.3 | 30.1 | 29.9 | 29.7 | 29.4 | 29.2 | 29 | 28.8 | 28.6 | 28.4 | 28.2 | 28 | 27.8 | 27.6 | 27.4 | 27.3
| 29.2BL | Measured personal washing | Input | l/h/d | 1 | 59.4 | 59.4 | 59.7 | 60 | 60.2 | 60.4 | 60.5 | 60.6 | 60.7 | 60.8 | 60.9 | 61 | 61 | 61.2 | 61.3 | 61.4 | 61.6 | 61.8 | 62 | 62.2 | 62.4 | 62.6 | 62.9 | 63.1 | 63.3 | 63.6 | 63.8 | 64.1 | 64.4
| 29.3BL | Measured clothes washing | Input | l/h/d | 1 | 18.3 | 18.3 | 18.2 | 18.2 | 18.2 | 18.3 | 18.2 | 18.2 | 18.2 | 18.2 | 18.2 | 18.2 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1 | 18.1
| 29.4BL | Measured dish washing | Input | l/h/d | 1 | 11.6 | 11.6 | 11.4 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.4 | 11.4 | 11.4 | 11.4 | 11.4 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.3 | 11.2 | 11.2 | 11.2
| 29.5BL | Measured miscellaneous internal use | Input | l/h/d | 1 | 9.2 | 9.2 | 9.1 | 9.2 | 9.2 | 9.2 | 9.2 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9.1 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9 | 9
| 29.6BL | Measured external use | Input | l/h/d | 1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1 | 2.1
| 30BL | Unmeasured Household - PCC | (26BL*1,000,000)/(52BL*1,000) | l/h/d | 1 | 146.5 | 146.5 | 146.6 | 147 | 147.3 | 147.5 | 147.8 | 147.9 | 148.1 | 148.2 | 148.3 | 148.5 | 148.7 | 148.9 | 149.1 | 149.3 | 149.6 | 149.8 | 150 | 150.2 | 150.5 | 150.6 | 150.8 | 150.9 | 151.1 | 151.3 | 151.4 | 151.5 | 151.7
| 30.1BL | Unmeasured toilet flushing | Input | l/h/d | 1 | 42.5 | 42.5 | 42.7 | 42.7 | 42.6 | 42.5 | 42.4 | 42.3 | 42.2 | 42 | 41.9 | 41.8 | 41.7 | 41.5 | 41.4 | 41.3 | 41.2 | 41.1 | 41 | 40.8 | 40.7 | 40.6 | 40.5 | 40.3 | 40.2 | 40 | 39.9 | 39.7 | 39.6
| 30.2BL | Unmeasured personal washing | Input | l/h/d | 1 | 51.7 | 51.7 | 51.6 | 51.8 | 51.9 | 52 | 52.1 | 52.2 | 52.2 | 52.3 | 52.3 | 52.5 | 52.5 | 52.6 | 52.7 | 52.8 | 53 | 53.1 | 53.2 | 53.3 | 53.4 | 53.5 | 53.6 | 53.7 | 53.8 | 54 | 54 | 54.1 | 54.2
| 30.3BL | Unmeasured clothes washing | Input | l/h/d | 1 | 18.3 | 18.3 | 18.3 | 18.4 | 18.5 | 18.6 | 18.7 | 18.8 | 18.9 | 18.9 | 19 | 19.1 | 19.2 | 19.3 | 19.4 | 19.4 | 19.5 | 19.6 | 19.7 | 19.8 | 19.9 | 19.9 | 20 | 20.1 | 20.2 | 20.2 | 20.3 | 20.4 | 20.4
| 30.4BL | Unmeasured dish washing | Input | l/h/d | 1 | 13.7 | 13.7 | 13.7 | 13.7 | 13.8 | 13.9 | 13.9 | 14 | 14 | 14.1 | 14.1 | 14.2 | 14.2 | 14.3 | 14.3 | 14.4 | 14.4 | 14.5 | 14.5 | 14.6 | 14.6 | 14.7 | 14.7 | 14.8 | 14.8 | 14.9 | 14.9 | 15 | 15
| 30.5BL | Unmeasured miscellaneous internal use | Input | l/h/d | 1 | 10.6 | 10.6 | 10.5 | 10.6 | 10.6 | 10.7 | 10.7 | 10.8 | 10.8 | 10.9 | 10.9 | 10.9 | 11 | 11 | 11.1 | 11.1 | 11.1 | 11.2 | 11.2 | 11.3 | 11.3 | 11.3 | 11.4 | 11.4 | 11.5 | 11.5 | 11.5 | 11.6 | 11.6
| 30.6BL | Unmeasured external use | Input | l/h/d | 1 | 9.7 | 9.7 | 9.7 | 9.7 | 9.8 | 9.8 | 9.9 | 9.9 | 10 | 10 | 10 | 10.1 | 10.1 | 10.2 | 10.2 | 10.3 | 10.3 | 10.4 | 10.4 | 10.4 | 10.5 | 10.5 | 10.6 | 10.6 | 10.6 | 10.7 | 10.7 | 10.8 | 10.8
| 31BL | Average Household - PCC | ((25BL+26BL)*1,000,000))/(51BL+52BL*1,000) | l/h/d | 1 | 143.3424 | 143.3424 | 143.1894 | 143.382 | 143.4073 | 143.4074 | 143.3186 | 143.2062 | 143.1126 | 142.9936 | 142.8873 | 142.7671 | 142.6405 | 142.5559 | 142.4904 | 142.4641 | 142.473 | 142.4928 | 142.5014 | 142.5118 | 142.5294 | 142.5505 | 142.5517 | 142.535 | 142.5843 | 142.5872 | 142.5864 | 142.5945 | 142.6008
| 32BL | Water Taken Unbilled | Input | Ml/d | 2 | 2.45 | 2.45 | 2.4499 | 2.4499 | 2.4499 | 2.4499 | 2.4499 | 2.4499 | 2.4499 | 2.4499 | 2.4499 | 2.4499 | 2.4499 | 2.4499 | 2.4499 | 2.4499 | 2.4499 | 2.4499 | 2.4499 | 2.4499 | 2.4499 | 2.4499 | 2.4499 | 2.4499 | 2.4499 | 2.4499 | 2.4499 | 2.4499 | 2.4499
| 33BL | Distribution System Operational Use | Input | Ml/d | 2 | 0.43 | 0.43 | 0.42897 | 0.42897 | 0.42897 | 0.42897 | 0.42897 | 0.42897 | 0.42897 | 0.42897 | 0.42897 | 0.42897 | 0.42897 | 0.42897 | 0.42897 | 0.42897 | 0.42897 | 0.42897 | 0.42897 | 0.42897 | 0.42897 | 0.42897 | 0.42897 | 0.42897 | 0.42897 | 0.42897 | 0.42897 | 0.42897 | 0.42897
Leakage | 34BL | Measured Non Household - USPL | Input | Ml/d | 2 | 0.28 | 0.28 | 0.28 | 0.28 | 0.27 | 0.27 | 0.26 | 0.26 | 0.25 | 0.25 | 0.25 | 0.24 | 0.24 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.23 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21
| 35BL | Unmeasured Non Household - USPL | Input | Ml/d | 2 | 0.05 | 0.05 | 0.04 | 0.04 | 0.04 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
| 36BL | Measured Household - USPL | Input | Ml/d | 2 | 1.79 | 1.79 | 1.79 | 1.79 | 1.84 | 1.9 | 1.99 | 2.07 | 2.15 | 2.23 | 2.31 | 2.46 | 2.6 | 2.73 | 2.86 | 2.97 | 3.08 | 3.18 | 3.28 | 3.37 | 3.46 | 3.54 | 3.62 | 3.69 | 3.76 | 3.83 | 3.9 | 3.96 | 4.02
| 37BL | Unmeasured Household - USPL | Input | Ml/d | 2 | 6.12 | 6.12 | 6.1 | 6.08 | 6.06 | 6.04 | 6.02 | 6 | 5.99 | 5.97 | 5.96 | 5.95 | 5.93 | 5.92 | 5.91 | 5.9 | 5.89 | 5.88 | 5.87 | 5.86 | 5.85 | 5.85 | 5.84 | 5.83 | 5.82 | 5.82 | 5.81 | 5.81 | 5.8
| 38BL | Void Properties - USPL | Input | Ml/d | 2 | 0.28 | 0.28 | 0.27 | 0.28 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27
| 39BL | Distribution Losses | Input | Ml/d | 2 | 26.52 | 26.52 | 26.47 | 26.42 | 26.42 | 26.42 | 26.42 | 26.42 | 26.42 | 26.42 | 26.42 | 26.42 | 26.42 | 26.42 | 26.42 | 26.42 | 26.42 | 26.42 | 26.42 | 26.42 | 26.42 | 26.42 | 26.42 | 26.42 | 26.42 | 26.42 | 26.42 | 26.42 | 26.42
| 40BL | Total Leakage | sum(34BL:39BL) | Ml/d | 2 | 35.04 | 35.04 | 34.95 | 34.89 | 34.9 | 34.93 | 34.99 | 35.05 | 35.11 | 35.17 | 35.24 | 35.37 | 35.49 | 35.61 | 35.73 | 35.82 | 35.92 | 36.01 | 36.1 | 36.17 | 36.25 | 36.33 | 36.4 | 36.46 | 36.51 | 36.58 | 36.64 | 36.7 | 36.75
| 41BL | Total Leakage | (40BL*1,000,000)/(48BL*1,000) | l/prop/d | 2 | 109.6302 | 109.6302 | 108.201 | 106.805 | 105.7864 | 104.9138 | 104.1865 | 103.5175 | 102.9076 | 102.3365 | 101.8762 | 101.6117 | 101.3392 | 101.0987 | 100.8895 | 100.5897 | 100.2988 | 99.9889 | 99.6907 | 99.3381 | 99.014 | 98.696 | 98.3465 | 97.9791 | 97.5838 | 97.2484 | 96.8876 | 96.5281 | 96.1463
Customer: Properties | 42BL | Measured non-households - properties | Input (total, excluding voids) | 000's | 2 | 13.82 | 13.82 | 13.95 | 13.82 | 13.57 | 13.33 | 13.12 | 12.91 | 12.71 | 12.53 | 12.35 | 12.19 | 12.04 | 11.9 | 11.76 | 11.63 | 11.51 | 11.39 | 11.28 | 11.17 | 11.06 | 10.96 | 10.86 | 10.77 | 10.68 | 10.59 | 10.51 | 10.44 | 10.37
| 43BL | Unmeasured non-households - properties | Input (total, excluding voids) | 000's | 2 | 1.81 | 1.81 | 1.81 | 1.81 | 1.77 | 1.74 | 1.72 | 1.69 | 1.66 | 1.64 | 1.62 | 1.59 | 1.57 | 1.56 | 1.54 | 1.52 | 1.5 | 1.49 | 1.47 | 1.46 | 1.45 | 1.43 | 1.42 | 1.41 | 1.4 | 1.39 | 1.38 | 1.37 | 1.36
| 44BL | All void non-households - properties | Input (voids in each year) | 000's | 2 | 3.62 | 3.62 | 3.62 | 3.62 | 3.55 | 3.55 | 3.49 | 3.44 | 3.39 | 3.34 | 3.29 | 3.25 | 3.21 | 3.18 | 3.14 | 3.11 | 3.07 | 3.04 | 3.01 | 2.99 | 2.96 | 2.93 | 2.91 | 2.88 | 2.86 | 2.84 | 2.82 | 2.8 | 2.78
| 45BL | Total measured households - properties (excl void) | Pre-plan year = input. Forecast years = Previous year 45BL + sum(45.1BL:45.6BL) | 000's | 2 | 89.29 | 89.29 | 95.03 | 100.87 | 106.5 | 111.72 | 116.71 | 121.44 | 125.91 | 130.16 | 134.07 | 137.83 | 141.41 | 144.81 | 148.06 | 151.24 | 154.46 | 157.58 | 160.61 | 163.58 | 166.53 | 169.43 | 172.28 | 175.09 | 177.86 | 180.6 | 183.3 | 185.97 | 188.61
| 45.1BL | New build properties - properties | Input (new builds in each year) | 000's | 2 | 0 | 0 | 3.42 | 3.66 | 3.58 | 3.29 | 3.17 | 3.02 | 2.86 | 2.73 | 2.48 | 2.41 | 2.3 | 2.19 | 2.11 | 2.1 | 2.2 | 2.16 | 2.12 | 2.11 | 2.13 | 2.12 | 2.11 | 2.11 | 2.11 | 2.11 | 2.1 | 2.1 | 2.1
| 45.2BL | Meter optants - properties | Input (meter optants in each year) | 000's | 2 | 0 | 0 | 2.32 | 2.18 | 2.05 | 1.93 | 1.82 | 1.71 | 1.61 | 1.52 | 1.43 | 1.35 | 1.28 | 1.21 | 1.14 | 1.08 | 1.02 | 0.96 | 0.91 | 0.86 | 0.82 | 0.78 | 0.74 | 0.7 | 0.66 | 0.63 | 0.6 | 0.57 | 0.54
| 45.3BL | Compulsory metering - properties | Input (compulsory meters in each year) | 000's | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 45.4BL | Metering on change of occupancy - properties | Input (change of occupancy meters in each year) | 000's | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 45.5BL | Selective metering - properties | Input (selective meters in each year) | 000's | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 45.6BL | Other changes to existing metering - properties | Input (other changes to meters in each year) | 000's | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 45.7BL | Measured void households - properties | Input (voids in each year) | 000's | 2 | 1.49 | 1.49 | 1.7 | 1.8 | 1.87 | 1.93 | 1.99 | 2.05 | 2.1 | 2.15 | 2.2 | 2.24 | 2.29 | 2.33 | 2.37 | 2.41 | 2.45 | 2.49 | 2.53 | 2.57 | 2.61 | 2.65 | 2.7 | 2.74 | 2.78 | 2.82 | 2.86 | 2.9 | 2.94
| 46BL | Unmeasured households - properties (excl void) | Input (total) | 000's | 2 | 204.16 | 204.16 | 201.84 | 199.66 | 197.61 | 195.68 | 193.86 | 192.15 | 190.54 | 189.02 | 187.58 | 186.23 | 184.96 | 183.75 | 182.61 | 181.54 | 180.52 | 179.55 | 178.64 | 177.78 | 176.96 | 176.18 | 175.45 | 174.75 | 174.09 | 173.46 | 172.86 | 172.3 | 171.76
| 47BL | Unmeasured void households - properties | Input (voids in each year) | 000's | 2 | 5.43 | 5.43 | 5.06 | 5.09 | 5.04 | 4.99 | 4.95 | 4.91 | 4.87 | 4.83 | 4.8 | 4.76 | 4.73 | 4.7 | 4.67 | 4.65 | 4.62 | 4.6 | 4.58 | 4.56 | 4.54 | 4.52 | 4.5 | 4.48 | 4.47 | 4.45 | 4.44 | 4.42 | 4.41
| 48BL | Total Resource Zone Properties (incl voids) | SUM(42BL:45BL)+45.7BL+46BL+47BL | 000's | 2 | 319.62 | 319.62 | 323.01 | 326.67 | 329.91 | 332.94 | 335.84 | 338.59 | 341.18 | 343.67 | 345.91 | 348.09 | 350.21 | 352.23 | 354.15 | 356.1 | 358.13 | 360.14 | 362.12 | 364.11 | 366.11 | 368.1 | 370.12 | 372.12 | 374.14 | 376.15 | 378.17 | 380.2 | 382.23
Customer: Population | 49BL | Measured Non Household - Population | Input (total) | 000's | 2 | 12.34 | 12.34 | 12.41 | 12.5 | 12.61 | 12.7 | 12.86 | 13.02 | 13.18 | 13.34 | 13.46 | 13.66 | 13.87 | 14.08 | 14.3 | 14.53 | 14.87 | 15.14 | 15.38 | 15.58 | 15.75 | 15.93 | 16.11 | 16.29 | 16.47 | 16.65 | 16.84 | 17.02 | 17.21
| 50BL | Unmeasured Non Household - Population | Input (total) | 000's | 2 | 1.61 | 1.61 | 1.62 | 1.63 | 1.65 | 1.66 | 1.68 | 1.7 | 1.72 | 1.74 | 1.76 | 1.78 | 1.81 | 1.84 | 1.87 | 1.9 | 1.94 | 1.98 | 2.01 | 2.04 | 2.06 | 2.08 | 2.11 | 2.13 | 2.15 | 2.18 | 2.2 | 2.23 | 2.25
| 51BL | Measured Household - Population | Input (total) | 000's | 2 | 172.76 | 172.76 | 185.33 | 197.89 | 209.87 | 220.96 | 231.56 | 241.62 | 251.07 | 260.08 | 268.3 | 276.13 | 283.56 | 290.52 | 297.15 | 303.56 | 309.92 | 316.08 | 322.01 | 327.83 | 333.55 | 339.13 | 344.63 | 350.07 | 355.3 | 360.49 | 365.59 | 370.61 | 375.56
| 52BL | Unmeasured Household - Population | Input (total) | 000's | 2 | 539.66 | 539.66 | 532.81 | 526.12 | 519.73 | 513.73 | 508.26 | 503.18 | 498.34 | 493.87 | 489.57 | 485.39 | 481.51 | 477.74 | 474.13 | 470.67 | 467.28 | 464.1 | 461.07 | 458.21 | 455.48 | 452.87 | 450.45 | 448.19 | 445.91 | 443.79 | 441.78 | 439.87 | 438.04
| 53BL | Total Resource Zone Population | Sum(49BL:52BL) | 000's | 2 | 726.37 | 726.37 | 732.17 | 738.14 | 743.86 | 749.05 | 754.36 | 759.52 | 764.31 | 769.03 | 773.09 | 776.96 | 780.75 | 784.18 | 787.45 | 790.66 | 794.01 | 797.3 | 800.47 | 803.66 | 806.84 | 810.01 | 813.3 | 816.68 | 819.83 | 823.11 | 826.41 | 829.73 | 833.06
Occupancy | 54BL | Measured Household - Occupancy Rate (average) (excl voids) | 51BL/45BL | h/prop | 1 | 1.9348 | 1.9348 | 1.9502 | 1.9618 | 1.9706 | 1.9778 | 1.9841 | 1.9896 | 1.994 | 1.9982 | 2.0012 | 2.0034 | 2.0052 | 2.0062 | 2.007 | 2.0071 | 2.0065 | 2.0058 | 2.0049 | 2.0041 | 2.0029 | 2.0016 | 2.0004 | 1.9994 | 1.9976 | 1.9961 | 1.9945 | 1.9928 | 1.9912
| 55BL | Unmeasured Household - Occupancy Rate | 52BL/46BL | h/prop | 1 | 2.6433 | 2.6433 | 2.6398 | 2.6351 | 2.6301 | 2.6254 | 2.6218 | 2.6187 | 2.6154 | 2.6128 | 2.6099 | 2.6064 | 2.6033 | 2.5999 | 2.5964 | 2.5927 | 2.5885 | 2.5848 | 2.581 | 2.5774 | 2.5739 | 2.5705 | 2.5674 | 2.5647 | 2.5614 | 2.5585 | 2.5557 | 2.5529 | 2.5503
Metering | 56BL | Total Household Metering penetration (excl. voids) | 45BL/45BL+46BL | % | 0 | 30.43% | 30.43% | 32.01% | 33.56% | 35.02% | 36.34% | 37.58% | 38.73% | 39.79% | 40.78% | 41.68% | 42.53% | 43.33% | 44.07% | 44.78% | 45.45% | 46.11% | 46.74% | 47.34% | 47.92% | 48.48% | 49.02% | 49.54% | 50.05% | 50.54% | 51.01% | 51.47% | 51.91% | 52.34%
| 57BL | Total Household Metering penetration (incl. voids) | 45BL/(45BL+45.7BL+46BL+47BL) | % | 0 | 29.73% | 29.73% | 31.3% | 32.81% | 34.24% | 35.54% | 36.76% | 37.88% | 38.93% | 39.91% | 40.79% | 41.63% | 42.42% | 43.15% | 43.84% | 44.5% | 45.16% | 45.78% | 46.37% | 46.94% | 47.49% | 48.03% | 48.54% | 49.04% | 49.52% | 49.98% | 50.43% | 50.87% | 51.29%
|  | Company: | Portsmouth Water
|  | Resource Zone Name: | Company
|  | Resource Zone Number: | PRT 1
|  | Planning Scenario Name: | Dry Year Annual Average - benchmarking data
|  | Chosen Level of Service: | 1 in 200

## 4. BL SDB
Table 4: Baseline supply demand balance
| Row ref | Component | Derivation | Unit | Decimal places | 2017/18 | For info 2017-18 | For info 2018-19 | For info 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-2030 | 2030-2031 | 2031-2032 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
SDB | 11BL | Distribution input | 19BL+20BL+21BL+22BL+32BL+33BL+38BL+39BL | Ml/d | 2 | 174.09 | 174.09 | 174.5489 | 175.2789 | 175.9289 | 176.5089 | 177.0589 | 177.5589 | 178.0389 | 178.4689 | 178.8289 | 179.2089 | 179.5489 | 179.8789 | 180.1889 | 180.4989 | 180.8389 | 181.1789 | 181.4989 | 181.8189 | 182.1689 | 182.5489 | 182.9089 | 183.2689 | 183.6389 | 183.9989 | 184.3589 | 184.7189 | 185.0789
| 12BL | Water Available For Use (own sources) | (7BL+8BL)-(9BL+10BL) | Ml/d | 2 | 175.34 | 175.34 | 175.34 | 175.18 | 175.1445 | 175.109 | 175.0735 | 174.588 | 174.5525 | 174.517 | 174.4815 | 174.446 | 174.4105 | 173.235 | 173.1995 | 173.164 | 173.1285 | 173.093 | 173.0575 | 173.022 | 172.9865 | 172.951 | 172.9155 | 172.88 | 172.8445 | 172.809 | 172.7735 | 172.738 | 172.7025
| 13BL | Total Water Available For Use | 12BL+(2BL+3BL)-(5BL+6BL) | Ml/d | 2 | 160.34 | 160.34 | 160.34 | 152.68 | 145.1445 | 145.109 | 145.0735 | 144.588 | 135.5525 | 135.517 | 135.4815 | 135.446 | 135.4105 | 113.235 | 113.1995 | 113.164 | 113.1285 | 113.093 | 113.0575 | 113.022 | 112.9865 | 112.951 | 112.9155 | 112.88 | 112.8445 | 112.809 | 112.7735 | 112.738 | 112.7025
| 14BL | Target headroom (climate change component) | Input | Ml/d | 2 | 1.578 | 1.6306 | 1.6832 | 1.7523 | 1.8156 | 1.785 | 1.8756 | 1.9795 | 2.128 | 1.9461 | 2.116 | 2.2878 | 2.5578 | 2.4897 | 2.2616 | 2.5605 | 2.806 | 3.0221 | 3.1584 | 2.9498 | 3.4 | 3.5853 | 3.77 | 3.9114 | 3.6828 | 3.817 | 4.0656 | 4.2294 | 4.3964
| 15BL | Target headroom (All other components) | Input | Ml/d | 2 | 3.682 | 3.6294 | 3.5768 | 3.5577 | 3.5244 | 3.315 | 3.3344 | 3.3705 | 3.472 | 3.0439 | 3.174 | 3.2922 | 3.5322 | 3.3003 | 2.8784 | 3.1295 | 3.294 | 3.4079 | 3.4216 | 3.0702 | 3.4 | 3.4447 | 3.48 | 3.4686 | 3.1372 | 3.123 | 3.1944 | 3.1906 | 3.1836
| 16BL | Target Headroom | 14BL+15BL | Ml/d | 2 | 5.26 | 5.26 | 5.26 | 5.31 | 5.34 | 5.1 | 5.21 | 5.35 | 5.6 | 4.99 | 5.29 | 5.58 | 6.09 | 5.79 | 5.14 | 5.69 | 6.1 | 6.43 | 6.58 | 6.02 | 6.8 | 7.03 | 7.25 | 7.38 | 6.82 | 6.94 | 7.26 | 7.42 | 7.58
| 17BL | Available Headroom | 13BL-11BL | Ml/d | 2 | -13.75 | -13.75 | -14.2089 | -22.5989 | -30.7844 | -31.3999 | -31.9854 | -32.9709 | -42.4864 | -42.9519 | -43.3474 | -43.7629 | -44.1384 | -66.6439 | -66.9894 | -67.3349 | -67.7104 | -68.0859 | -68.4414 | -68.7969 | -69.1824 | -69.5979 | -69.9934 | -70.3889 | -70.7944 | -71.1899 | -71.5854 | -71.9809 | -72.3764
| 18BL | Supply Demand Balance | 17BL-16BL | Ml/d | 2 | -19.01 | -19.01 | -19.4689 | -27.9089 | -36.1244 | -36.4999 | -37.1954 | -38.3209 | -48.0864 | -47.9419 | -48.6374 | -49.3429 | -50.2284 | -72.4339 | -72.1294 | -73.0249 | -73.8104 | -74.5159 | -75.0214 | -74.8169 | -75.9824 | -76.6279 | -77.2434 | -77.7689 | -77.6144 | -78.1299 | -78.8454 | -79.4009 | -79.9564
|  | Company: | Portsmouth Water
|  | Resource Zone Name: | Company
|  | Resource Zone Number: | PRT 1
|  | Planning Scenario Name: | Dry Year Annual Average - benchmarking data
|  | Chosen Level of Service: | 1 in 200
README

## 5. Feasible Options
Table 5: Feasible options detailed costs | [18 empty] | ENTER DISCOUNT RATE % |  |  |  | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3.5% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 3% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5% | 2.5%
Detail the gains in WAFU / savings in demand, and the costs of feasible options under capacity use scenario | [18 empty] | ENTER DISCOUNT PERIOD (YRS) | 80 |  | 1 | 0.96618 | 0.93351 | 0.90194 | 0.87144 | 0.84197 | 0.8135 | 0.78599 | 0.75941 | 0.73373 | 0.70892 | 0.68495 | 0.66178 | 0.6394 | 0.61778 | 0.59689 | 0.57671 | 0.5572 | 0.53836 | 0.52016 | 0.50257 | 0.48557 | 0.46915 | 0.45329 | 0.43796 | 0.42315 | 0.40884 | 0.39501 | 0.38165 | 0.36875 | 0.35801 | 0.34758 | 0.33746 | 0.32763 | 0.31809 | 0.30882 | 0.29983 | 0.29109 | 0.28261 | 0.27438 | 0.26639 | 0.25863 | 0.2511 | 0.24379 | 0.23669 | 0.22979 | 0.2231 | 0.2166 | 0.21029 | 0.20417 | 0.19822 | 0.19245 | 0.18684 | 0.1814 | 0.17612 | 0.17099 | 0.16601 | 0.16117 | 0.15648 | 0.15192 | 0.14749 | 0.1432 | 0.13903 | 0.13498 | 0.13105 | 0.12723 | 0.12352 | 0.11993 | 0.11643 | 0.11304 | 0.10975 | 0.10655 | 0.10345 | 0.10044 | 0.097511 | 0.095133 | 0.092813 | 0.090549 | 0.08834 | 0.086186 | Note: If option costs are required from beyond year 80 then the NPV calculation formula must be amended manually to cover the extended period
[22 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 103 | 104
Row ref | Option name | Option reference no. | Type of option | Preferred Option (Y/N) | Earliest potential option start date (Year) | Costs based on capacity | WAFU on full implementation (Ml/d) | NPV of WAFU (Ml) | CAPEX NPV (£000) | OPEX NPV (£000) | NPV of opex savings (£000) | NPV of carbon (£000) | Social & Env. NPV (£000) | TOTAL NPV (£000) | AIC (p/m3) | AISC (p/m3) | Scope confidence (score 1 to 5) | Cost confidence (score 1 to 5) | Cost component | Derivation | Unit | Year 1 | Year 2 | Year 3 | Year 4 | Year 5 | Year 6 | Year 7 | Year 8 | Year 9 | Year 10 | Year 11 | Year 12 | Year 13 | Year 14 | Year 15 | Year 16 | Year 17 | Year 18 | Year 19 | Year 20 | Year 21 | Year 22 | Year 23 | Year 24 | Year 25 | Year 26 | Year 27 | Year 28 | Year 29 | Year 30 | Year 31 | Year 32 | Year 33 | Year 34 | Year 35 | Year 36 | Year 37 | Year 38 | Year 39 | Year 40 | Year 41 | Year 42 | Year 43 | Year 44 | Year 45 | Year 46 | Year 47 | Year 48 | Year 49 | Year 50 | Year 51 | Year 52 | Year 53 | Year 54 | Year 55 | Year 56 | Year 57 | Year 58 | Year 59 | Year 60 | Year 61 | Year 62 | Year 63 | Year 64 | Year 65 | Year 66 | Year 67 | Year 68 | Year 69 | Year 70 | Year 71 | Year 72 | Year 73 | Year 74 | Year 75 | Year 76 | Year 77 | Year 78 | Year 79 | Year 80 | Year 81 | Year 82 | Year 83 | Year 84 | Year 85 | Year 86 | Year 87 | Year 88 | Year 89 | Year 90 | Year 91 | Year 92 | Year 93 | Year 94 | Year 95 | Year 96 | Year 97 | Year 98 | Year 99 | Year 100 | Year 101 | Year 102 | Year 103 | Year 104
58a | RESOURCE SIDE | bar: 1 to 80
58.1a | Options to increase raw water abstractions | [17 empty] | Total Mld for SDB component |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.1x | Havant Thicket Reservoir | R013 | New reservoir | Y | 2029/30 | Capacity | 23 | 173407.6408 | 110251.1644 | 13465.1498 | 0 | 7885.6082 | -58902.3105 | 72699.6119 | 71.3442 | 41.9241 | 1 | 1 | Gains in WAFU / Savings in demand | Input | Ml/d | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 24.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.1x | Source J Borehole | R022a | GW enhancement | Y | 2024/25 | Capacity | 12.5 | 117018.4448 | 2083.4564 | 4019.1399 | 0 | 1146.7231 | 0 | 7249.3194 | 5.2151 | 6.195 | 3 | 3 | Gains in WAFU / Savings in demand | Input | Ml/d | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.1x | Source C DO Recovery | R024a | GW enhancement | Y | 2019/20 | Capacity | 4 | 36128.1641 | 9.4408 | 4823.0063 | 0 | 351.678 | 0 | 5184.1252 | 13.3758 | 14.3493 | 2 | 3 | Gains in WAFU / Savings in demand | Input | Ml/d | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.1x | Source O DO Recovery | R021a | GW enhancement | Y | 2019/20 | Capacity | 1.8 | 16850.6561 | 834.986 | 0 | 227.6133 | 0 | 0 | 1062.5992 | 6.306 | 6.306 | 2 | 3 | Gains in WAFU / Savings in demand | Input | Ml/d | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
58.1x | Source H DO Recovery | R023a | GW enhancement | Y | 2019/20 | Capacity | 2 | 18722.9512 | 852.0198 | 366.512 | 0 | 8.1173 | 0 | 1226.6491 | 6.5082 | 6.5516 | 2 | 3 | Gains in WAFU / Savings in demand | Input | Ml/d | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.1x | Source S Drought Permit | R068 | GW enhancement | Y | 2018/19 | Capacity | 8.5 | 88575.0058 | 9.4408 | 3949.1541 | 0 | 754.3105 | 0 | 4712.9055 | 4.4692 | 5.3208 | 2 | 3 | Gains in WAFU / Savings in demand | Input | Ml/d | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.2a | Options to increase raw imports | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.3a | Options to increase potable imports | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.4a | Options to reduce raw water losses and operational use | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.5a | Options to reduce raw water exports | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.6a | Options to reduce potable water exports | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.7a | Other options to increase Deployable Output | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
59a | DISTRIBUTION SIDE | bar: 1 to 80
59.1a | Options to reduce Distribution Losses | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.1x | District Metering Phase 1 | D005 | Active leakage management | N | 2020/21 | Capacity | 5.1 | 50413.3008 | 996.7436 | 3625.4282 | 0 | -101.277 | 2161.2983 | 6682.1932 | 9.1686 | 13.2548 | 3 | 2 | Gains in WAFU / Savings in demand | Input | Ml/d | 1 | 2 | 3 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5
| District Metering Phase 2 | D011 | Active leakage management | N | 2025/26 | Capacity | 10 | 89167.5609 | 6489.2182 | 11332.4204 | 0 | -17.1151 | 9892.1509 | 27696.6745 | 19.9867 | 31.0614 | 3 | 2 | Gains in WAFU / Savings in demand | Input | Ml/d | 2 | 4 | 6 | 8 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10
| Permanent Noise Loggers Phase 1 | D004a | Active leakage management | Y | 2020/21 | Capacity | 5.4 | 52421.7303 | 5686.9769 | 1134.0682 | 0 | -112.3755 | 98.9039 | 6807.5735 | 13.0119 | 12.9862 | 3 | 2 | Gains in WAFU / Savings in demand | Input | Ml/d | 1.08 | 2.16 | 3.24 | 4.32 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4
58.1x | Permanent Noise Loggers Phase 2 | D004b | Active leakage management | Y | 2025/26 | Capacity | 5.4 | 34041.3826 | 6984.5842 | 1211.9325 | 0 | -73.1844 | 133.2038 | 8256.536 | 24.0781 | 24.2544 | 3 | 2 | Gains in WAFU / Savings in demand | Input | Ml/d | 0.27 | 0.54 | 0.81 | 1.08 | 1.35 | 1.62 | 1.89 | 2.16 | 2.43 | 2.7 | 2.97 | 3.24 | 3.51 | 3.78 | 4.05 | 4.32 | 4.59 | 4.86 | 5.13 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4 | 5.4
59.2a | Options to reduce Distribution System Operating Use (DSOU) losses | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
60a | PRODUCTION SIDE | bar: 1 to 80
60.1a | Options to reduce treatment works losses | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
60.2a | Options to reduce outage | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61a | CUSTOMER SIDE | bar: 1 to 80
61.1a | Options to change volume delivered to measured non households | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.1x | Non Essential Use Ban | C080 | Drought Measure | Y | 2018/19 | Capacity | 8.8028 | 90207.3724 | 179.733 | 220.7753 | 0 | -215.5113 | 0 | 184.997 | 0.44399 | 0.20508 | 2 | 3 | Gains in WAFU / Savings in demand | Input | Ml/d | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1 | 8.1
61.2a | Options to change volume delivered to unmeasured non households | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61.3a | Options to change volume delivered to measured households | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61.4a | Options to change volume delivered to unmeasured households | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.1x | Retrofitting Existing Toilets | C034 | Retrofitting indoor water efficiency devices | Y | 2018/19 | Capacity | 0.11198 | 848.0916 | 92.2427 | 1.7086 | 0 | -0.35192 | 1.4388 | 95.0382 | 11.078 | 11.2061 | 3 | 3 | Gains in WAFU / Savings in demand | Input | Ml/d | 0.01 | 0.02 | 0.03 | 0.04 | 0.04 | 0.04 | 0.04 | 0.05 | 0.05 | 0.05 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.06 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07 | 0.07
58.1x | Install Spray Taps | C040 | Retrofitting indoor water efficiency devices | Y | 2018/19 | Capacity | 0.073169 | 543.1554 | 2302.0676 | 3.94 | 0 | 0 | 8.2947 | 2314.3023 | 424.5576 | 426.0848 | 3 | 3 | Gains in WAFU / Savings in demand | Input | Ml/d | 0 | 0.01 | 0.01 | 0.02 | 0.02 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.04 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05
58.1x | Household Water Efficiency Programme | C046 | Household water audit | Y | 2018/19 | Capacity | 1.2686 | 9417.4347 | 1144.4888 | 2.4484 | 0 | -3204.7521 | 10.309 | -2047.506 | 12.1789 | -21.7417 | 3 | 3 | Gains in WAFU / Savings in demand | Input | Ml/d | 0.07 | 0.14 | 0.23 | 0.33 | 0.43 | 0.45 | 0.5 | 0.54 | 0.58 | 0.61 | 0.64 | 0.67 | 0.69 | 0.71 | 0.73 | 0.75 | 0.76 | 0.77 | 0.78 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.2 | 1.2 | 1.2 | 1.2 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3
58.1x | Water Efficiency Appliance Subsidy | C026 | Other water efficiency | Y | 2018/19 | Capacity | 0.31131 | 2357.6859 | 413.4945 | 7.5939 | 0 | -768.1565 | 1.0658 | -346.0023 | 17.8602 | -14.6755 | 3 | 3 | Gains in WAFU / Savings in demand | Input | Ml/d | 0.11 | 0.21 | 0.31 | 0.31 | 0.3 | 0.3 | 0.29 | 0.29 | 0.29 | 0.28 | 0.28 | 0.27 | 0.27 | 0.27 | 0.26 | 0.26 | 0.26 | 0.25 | 0.25 | 0.25 | 0.24 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23 | 0.23
| Install Trigger Guns and Water Butts | C043 | Outdoor water efficiency devices | Y | 2018/19 | Capacity | 0.062369 | 155.2923 | 381.5866 | 1.0631 | 0 | 40.2183 | 2.2382 | 425.1062 | 246.4062 | 273.7459 | 3 | 3 | Gains in WAFU / Savings in demand | Input | Ml/d | 0 | 0.02 | 0.03 | 0.04 | 0.04 | 0.04 | 0.04 | 0.03 | 0.03 | 0.03 | 0.03 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.02 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.1x | Waterwise Programme | C046b | Customer education / awareness | Y | 2018/19 | Capacity | 1.2686 | 9417.4347 | 1144.4888 | 2.4484 | 0 | -3204.7521 | 10.309 | -2047.506 | 12.1789 | -21.7417 | 3 | 3 | Gains in WAFU / Savings in demand | Input | Ml/d | 0.07 | 0.14 | 0.23 | 0.33 | 0.43 | 0.45 | 0.5 | 0.54 | 0.58 | 0.61 | 0.64 | 0.67 | 0.69 | 0.71 | 0.73 | 0.75 | 0.76 | 0.77 | 0.78 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 1 | 1 | 1 | 1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.2 | 1.2 | 1.2 | 1.2 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3 | 1.3
58.1x | Metering on Change of Occupier (Phase 2) | C006b | Metering change of occupancy | Y | 2025/26 | Capacity | 4.6843 | 28244.4798 | 21589.1285 | 2842.1918 | -3847.1938 | -12665.5877 | 324.0341 | 8242.573 | 72.8784 | 29.183 | 3 | 2 | Gains in WAFU / Savings in demand | Input | Ml/d | 0 | 0 | 0 | 0 | 0 | 0.48566 | 0.9341 | 1.3476 | 1.7282 | 2.0779 | 2.3987 | 2.6923 | 2.9604 | 3.2045 | 3.4264 | 3.6272 | 3.8083 | 3.971 | 4.1165 | 4.2458 | 4.36 | 4.46 | 4.5468 | 4.6213 | 4.6843 | 4.6194 | 4.5553 | 4.4922 | 4.4299 | 4.3685 | 4.3079 | 4.2482 | 4.1893 | 4.1313 | 4.074 | 4.0175 | 3.9618 | 3.9069 | 3.8527 | 3.7993 | 3.7466 | 3.6947 | 3.6435 | 3.593 | 3.5432 | 3.494 | 3.4456 | 3.3978 | 3.3507 | 3.3043 | 3.2585 | 3.2133 | 3.1688 | 3.1248 | 3.0815 | 3.0388 | 2.9967 | 2.9551 | 2.9142 | 2.8738 | 2.8339 | 2.7946 | 2.7559 | 2.7177 | 2.68 | 2.6429 | 2.6062 | 2.5701 | 2.5345 | 2.4993 | 2.4647 | 2.4305 | 2.3968 | 2.3636 | 2.3308 | 2.2985 | 2.2667 | 2.2352 | 2.2042 | 2.1737
58.1x | Metering on Change of Occupier (Phase 1) | C006a | Metering change of occupancy | Y | 2020/21 | Capacity | 0.27866 | 2054.7731 | 968.886 | 188.6065 | -283.763 | -665.6119 | 23.8917 | 232.0093 | 42.5219 | 11.2912 | 3 | 2 | Gains in WAFU / Savings in demand | Input | Ml/d | 0.051988 | 0.10598 | 0.16185 | 0.21943 | 0.27866 | 0.2748 | 0.27099 | 0.26723 | 0.26353 | 0.25987 | 0.25627 | 0.25272 | 0.24921 | 0.24576 | 0.24235 | 0.23899 | 0.23568 | 0.23241 | 0.22919 | 0.22601 | 0.22288 | 0.21979 | 0.21674 | 0.21374 | 0.21078 | 0.20785 | 0.20497 | 0.20213 | 0.19933 | 0.19657 | 0.19384 | 0.19115 | 0.1885 | 0.18589 | 0.18331 | 0.18077 | 0.17827 | 0.17579 | 0.17336 | 0.17095 | 0.16858 | 0.16625 | 0.16394 | 0.16167 | 0.15943 | 0.15722 | 0.15504 | 0.15289 | 0.15077 | 0.14868 | 0.14662 | 0.14459 | 0.14258 | 0.14061 | 0.13866 | 0.13673 | 0.13484 | 0.13297 | 0.13113 | 0.12931 | 0.12752 | 0.12575 | 0.124 | 0.12229 | 0.12059 | 0.11892 | 0.11727 | 0.11564 | 0.11404 | 0.11246 | 0.1109 | 0.10936 | 0.10785 | 0.10635 | 0.10488 | 0.10342 | 0.10199 | 0.10058 | 0.099182 | 0.097807
58.1x | Smart Metering Trial (NFR) | C005 | Metering optants | Y | 2020/21 | Capacity | 0.077769 | 480.2595 | 3332.0603 | 43.691 | -532.2169 | -194.1195 | 9.3894 | 2658.8043 | 592.083 | 553.6183 | 3 | 3 | Gains in WAFU / Savings in demand | Input | Ml/d | 0.0036595 | 0.0072682 | 0.010827 | 0.014336 | 0.017797 | 0.02121 | 0.024575 | 0.027894 | 0.031167 | 0.034394 | 0.037577 | 0.040715 | 0.043811 | 0.046863 | 0.049872 | 0.052841 | 0.055768 | 0.058654 | 0.0615 | 0.064307 | 0.067075 | 0.069805 | 0.072497 | 0.075151 | 0.077769 | 0.076691 | 0.075627 | 0.074579 | 0.073545 | 0.072526 | 0.07152 | 0.070529 | 0.069551 | 0.068587 | 0.067636 | 0.066698 | 0.065774 | 0.064862 | 0.063963 | 0.063076 | 0.062202 | 0.061339 | 0.060489 | 0.05965 | 0.058823 | 0.058008 | 0.057204 | 0.056411 | 0.055629 | 0.054858 | 0.054097 | 0.053347 | 0.052608 | 0.051878 | 0.051159 | 0.05045 | 0.049751 | 0.049061 | 0.048381 | 0.04771 | 0.047049 | 0.046396 | 0.045753 | 0.045119 | 0.044493 | 0.043877 | 0.043268 | 0.042669 | 0.042077 | 0.041494 | 0.040918 | 0.040351 | 0.039792 | 0.03924 | 0.038696 | 0.03816 | 0.037631 | 0.037109 | 0.036595 | 0.036087
| Void Metering | C084 | Metering compulsory | Y | 2020/21 | Capacity | 0.27895 | 1745.8602 | 1398.0983 | 174.5254 | -238.1731 | -750.0751 | 20.0565 | 604.4319 | 76.4351 | 34.6209 | 3 | 3 | Gains in WAFU / Savings in demand | Input | Ml/d | 0.013883 | 0.027515 | 0.0409 | 0.054042 | 0.067001 | 0.079723 | 0.092268 | 0.10458 | 0.11667 | 0.12852 | 0.14016 | 0.15158 | 0.16278 | 0.17377 | 0.18454 | 0.19505 | 0.20536 | 0.21541 | 0.22526 | 0.2348 | 0.24415 | 0.25325 | 0.26206 | 0.27062 | 0.27895 | 0.27509 | 0.27127 | 0.26751 | 0.2638 | 0.26015 | 0.25654 | 0.25298 | 0.24948 | 0.24602 | 0.24261 | 0.23924 | 0.23593 | 0.23266 | 0.22943 | 0.22625 | 0.22312 | 0.22002 | 0.21697 | 0.21396 | 0.211 | 0.20807 | 0.20519 | 0.20234 | 0.19954 | 0.19677 | 0.19404 | 0.19135 | 0.1887 | 0.18609 | 0.18351 | 0.18096 | 0.17845 | 0.17598 | 0.17354 | 0.17113 | 0.16876 | 0.16642 | 0.16412 | 0.16184 | 0.1596 | 0.15738 | 0.1552 | 0.15305 | 0.15093 | 0.14884 | 0.14677 | 0.14474 | 0.14273 | 0.14075 | 0.1388 | 0.13688 | 0.13498 | 0.13311 | 0.13126 | 0.12944
| Smart Metering Existing Households | C075 | Metering other selective | N | 2020/21 | Capacity | 1.4147 | 10002.9683 | 27558.2162 | 61.883 | -4737.2393 | -3731.1627 | -32.4933 | 19119.2039 | 228.7607 | 191.1353 | 3 | 3 | Gains in WAFU / Savings in demand | Input | Ml/d | 0.14 | 0.28 | 0.42 | 0.56 | 0.7 | 0.84 | 0.98 | 1.12 | 1.26 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4
| Smart Metering New Houses | C069 | Metering other selective | N | 2020/21 | Capacity | 0.23856 | 1770.9159 | 249.9935 | 20.5272 | -486.7734 | -605.3524 | -3.3575 | -824.9627 | -12.2113 | -46.584 | 3 | 3 | Gains in WAFU / Savings in demand | Input | Ml/d | 0.05 | 0.09 | 0.14 | 0.17 | 0.21 | 0.2 | 0.19 | 0.18 | 0.17 | 0.16 | 0.15 | 0.14 | 0.13 | 0.12 | 0.11 | 0.1 | 0.09 | 0.08 | 0.07 | 0.06 | 0.05 | 0.04 | 0.03 | 0.02 | 0.01 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Calls for Restraint | C078 | Drought Measure | Y | 2018/19 | Capacity | 4.627 | 47415.176 | 479.113 | 183.9794 | 0 | -13.1609 | 87.0151 | 736.9465 | 1.3985 | 1.5542 | 2 | 3 | Gains in WAFU / Savings in demand | Input | Ml/d | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3 | 4.3
58.1x | Hosepipe Ban | C079 | Drought Measure | Y | 2018/19 | Capacity | 9.0226 | 92459.5933 | 574.9356 | 201.9449 | 0 | -220.892 | 0 | 555.9884 | 0.84024 | 0.60133 | 2 | 3 | Gains in WAFU / Savings in demand | Input | Ml/d | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3 | 8.3
61.5a | Options to reduce water taken unbilled | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61.6a | Options impacting on measured Non Household - USPL | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61.7a | Options impacting on unmeasured Non Household - USPL | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61.8a | Options impacting on measured Household - USPL | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61.9a | Options impacting on unmeasured Household - USPL | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61.10a | Options impacting on Void properties - USPL | [20 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Company: | Portsmouth Water
| Resource Zone Name: | Company
| Resource Zone Number: | PRT 1
| Planning Scenario Name: | Dry Year Annual Average - benchmarking data
| Chosen Level of Service: | 1 in 200
Option Categories
Aquifer recharge
Bulk supply
Conjunctive use
Desalination
Effluent reuse
GW enhancement
GW new
Reservoir enlargement
New reservoir
SW enhancement
SW new
Active leakage management
Mains repair
Mains replacement (not trunk mains)
Pressure management
Other leakage control
Trunk mains renewal
Pumps
Service reservoir
Water treatment works loss recovery
Water treatment works capacity increase
Cistern displacement device
Household water audit
Commercial water audit
Customer education / awareness
Other water efficiency
Metering optants
Metering change of occupancy
Metering compulsory
Metering other selective
Supply pipe repairs / replacement
Outdoor water efficiency devices
Retrofitting indoor water efficiency devices
Alternative tariffs
Collaborative R&D
Note on DW1: Author: At year 126 this drops to 2%
Note on V2: The original formulae assumed 80 whatever number was put here. The formulae in this sheet will take account of the number.
Note on X2: Cells X2:CY2 contain a factor to calculate NPV based on variable discount rate - please do not adjust
Note on CY2: Formula can be copied across to the right if appraisal period extends beyond 80 years

## 6. Preferred (Scenario Yr)
DRY YEAR PLANNED GAINS IN WAFU OR SAVINGS IN DEMAND (Ml/d) - TO BE COMPLETED FOR ALL PREFERRED OPTIONS (WAFU gains for each year are individual year gains and not cumulative gains)
Row Ref | Option Name [Insert / delete non-numbered lines to suit] | Option Reference No. | Unit | Decimal places | 2017/18 | For info 2017-18 | For info 2018-19 | For info 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-2030 | 2030-2031 | 2031-2032 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
58 | Resource Management | - | Ml/d | 2 | 8.5 | 8.5 | 8.5 | 16.3 | 16.3 | 16.3 | 16.3 | 16.3 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 51.8 | 51.8 | 51.8 | 51.8 | 51.8 | 51.8 | 51.8 | 51.8 | 51.8 | 51.8 | 51.8 | 51.8 | 51.8 | 51.8 | 51.8 | 51.8
58.1 | Increase raw water abstractions | - | Ml/d | 2 | 8.5 | 8.5 | 8.5 | 16.3 | 16.3 | 16.3 | 16.3 | 16.3 | 28.8 | 28.8 | 28.8 | 28.8 | 28.8 | 51.8 | 51.8 | 51.8 | 51.8 | 51.8 | 51.8 | 51.8 | 51.8 | 51.8 | 51.8 | 51.8 | 51.8 | 51.8 | 51.8 | 51.8 | 51.8
- | Havant Thicket Reservoir | R013 | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23 | 23
| Source J Boreholes | R022a | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5 | 12.5
| Source C DO Recovery | R024a | Ml/d | 2 | 0 | 0 | 0 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4
| Source H DO Recovery | R023a | Ml/d | 2 | 0 | 0 | 0 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
| Source O DO Recovery | R021a | Ml/d | 2 | 0 | 0 | 0 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8 | 1.8
| Source S Drought Permit | R068 | Ml/d | 2 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5 | 8.5
- | (insert row above) | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: 2032-33 to 2044-45
58.2 | Raw water imports | - | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- |  |  | Ml/d | 2
- | (insert row above) | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: 2032-33 to 2044-45
58.3 | Potable water Imports (input reductions as -ve) | - | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- |  |  | Ml/d | 2
- | (insert row above) | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: 2032-33 to 2044-45
58.4 | Reduce raw water losses and operational use (input as -ve) | - | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- |  |  | Ml/d | 2
- | (insert row above) | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: 2032-33 to 2044-45
58.5 | Reduced raw water export (including non potable supplies) |  | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58.51 | Reduce raw water exports (input as -ve) | - | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- |  |  | Ml/d | 2
- | (insert row above) | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: 2032-33 to 2044-45
58.52 | Reduce non potable supplies (input as -ve) | - | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- |  |  | Ml/d | 2
- | (insert row above) | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: 2032-33 to 2044-45
58.6 | Reduce potable water exports (input as -ve) | - | Ml/d |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- |  |  | Ml/d | 2
- | (insert row above) | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: 2032-33 to 2044-45
58.7 | Other options to increase deployable output | - | Ml/d |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- |  |  | Ml/d | 2
- | (insert row above) | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: 2032-33 to 2044-45
59 | Distribution Side Management | - |  |  | 0 | 0 | 0 | -0.02 | -1.37 | -2.76 | -4.23 | -5.67 | -7.12 | -7.36 | -7.63 | -8.02 | -8.41 | -8.8 | -9.2 | -9.54 | -9.91 | -10.26 | -10.62 | -10.94 | -11.3 | -11.62 | -11.96 | -12.29 | -12.6 | -12.91 | -13.25 | -13.58 | -13.88
59.1 | Reduce distribution losses (input as -ve) | - | Ml/d | 2 | 0 | 0 | 0 | -0.02 | -1.37 | -2.76 | -4.23 | -5.67 | -7.12 | -7.36 | -7.63 | -8.02 | -8.41 | -8.8 | -9.2 | -9.54 | -9.91 | -10.26 | -10.62 | -10.94 | -11.3 | -11.62 | -11.96 | -12.29 | -12.6 | -12.91 | -13.25 | -13.58 | -13.88
| Permanent Noise Loggers (Phase 1) | D004a | Ml/d | 2 | 0 | 0 | 0 | -0.02 | -1.37 | -2.76 | -4.23 | -5.67 | -7.12 | -6.95 | -6.78 | -6.62 | -6.47 | -6.35 | -6.24 | -6.15 | -6.06 | -5.98 | -5.91 | -5.85 | -5.79 | -5.74 | -5.68 | -5.64 | -5.59 | -5.55 | -5.52 | -5.48 | -5.45
| Permanent Noise Loggers (Phase 2) | D004b | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.41 | -0.85 | -1.4 | -1.94 | -2.45 | -2.96 | -3.39 | -3.85 | -4.28 | -4.71 | -5.09 | -5.51 | -5.88 | -6.28 | -6.65 | -7.01 | -7.36 | -7.73 | -8.1 | -8.43
- | (insert row above) | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: 2032-33 to 2044-45
59.2 | Reduce distribution system operational use (DSOU) (input as -ve) | - | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- |  |  | Ml/d | 2
- | (insert row above) | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: 2032-33 to 2044-45
60 | Production Side Management, Specify Below.... | - |  | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
60.1 | Reduce treatment works losses (input as -ve) | - | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- |  |  | Ml/d | 2
- | (insert row above) | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: 2032-33 to 2044-45
60.2 | Reduce outages (input as -ve) | - | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- |  |  | Ml/d | 2
- | (insert row above) | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: 2032-33 to 2044-45
61 | Customer Side Management | - |  | 2 | -20.66 | -20.66 | -20.66 | -20.6583 | -21.5461 | -22.2146 | -22.9362 | -23.651 | -24.8613 | -25.4847 | -26.0396 | -26.5959 | -27.1132 | -27.5914 | -28.0605 | -28.5104 | -28.881 | -29.2822 | -29.6141 | -29.9567 | -30.2797 | -30.5632 | -30.8373 | -31.0917 | -31.3266 | -31.5418 | -31.7474 | -31.9433 | -32.1161
61.1 | Change volume delivered to measured non households (input reductions as -ve) | - | Ml/d | 2 | -8.1 | -8.1 | -8.1 | -8.1 | -8.1 | -8.1 | -8.1 | -8.1 | -8.1 | -8.1 | -8.1 | -8.1 | -8.1 | -8.1 | -8.1 | -8.1 | -8.1 | -8.1 | -8.1 | -8.1 | -8.1 | -8.1 | -8.1 | -8.1 | -8.1 | -8.1 | -8.1 | -8.1 | -8.1
- | Non Essential Use Bans | C080 | Ml/d | 2 | -8.1 | -8.1 | -8.1 | -8.1 | -8.1 | -8.1 | -8.1 | -8.1 | -8.1 | -8.1 | -8.1 | -8.1 | -8.1 | -8.1 | -8.1 | -8.1 | -8.1 | -8.1 | -8.1 | -8.1 | -8.1 | -8.1 | -8.1 | -8.1 | -8.1 | -8.1 | -8.1 | -8.1 | -8.1
- | (insert row above) | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: 2032-33 to 2044-45
61.2 | Change volume delivered to unmeasured non households (input reductions as -ve) | - | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- | (insert row above) | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: 2032-33 to 2044-45
61.3 | Change volume delivered to measured households (input reductions as -ve) | - | Ml/d | 2 | -2.32 | -2.32 | -2.46 | -2.59 | -2.0954 | -1.4717 | -0.88875 | -0.25981 | 0.17919 | 3.1382 | 5.7759 | 8.1539 | 10.3421 | 12.3905 | 14.2591 | 15.9979 | 17.6267 | 19.0958 | 20.4649 | 21.7342 | 22.9035 | 23.993 | 24.9725 | 25.8822 | 26.7219 | 27.5117 | 28.2115 | 28.8714 | 29.4814
| Retrofit Existing Toilets | C034 | Ml/d | 2 | 0 | 0 | 0 | 0 | -0.01 | -0.02 | -0.03 | -0.04 | -0.04 | -0.04 | -0.04 | -0.05 | -0.05 | -0.05 | -0.06 | -0.06 | -0.06 | -0.06 | -0.06 | -0.06 | -0.07 | -0.07 | -0.07 | -0.07 | -0.07 | -0.07 | -0.07 | -0.07 | -0.07
| Install Spray Taps | C040 | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | -0.01 | -0.01 | -0.02 | -0.03 | -0.03 | -0.03 | -0.03 | -0.03 | -0.04 | -0.04 | -0.04 | -0.04 | -0.04 | -0.04 | -0.04 | -0.04 | -0.04 | -0.05 | -0.05 | -0.05 | -0.05 | -0.05 | -0.05 | -0.05
| Trigger nozzles & water butts | C043 | Ml/d | 2 | 0 | 0 | 0 | 0 | -0.0053862 | -0.011662 | -0.018754 | -0.01981 | -0.020807 | -0.02175 | -0.024078 | -0.026106 | -0.027881 | -0.029471 | -0.030885 | -0.032142 | -0.033253 | -0.034239 | -0.035095 | -0.035838 | -0.036472 | -0.037014 | -0.037461 | -0.03783 | -0.038119 | -0.038342 | -0.038498 | -0.038599 | -0.038644
| Household Water Efficiency Programme | C046a | Ml/d | 2 | 0 | 0 | 0 | 0 | -0.07 | -0.14 | -0.23 | -0.33 | -0.44 | -0.45 | -0.5 | -0.55 | -0.58 | -0.62 | -0.65 | -0.67 | -0.7 | -0.72 | -0.73 | -0.75 | -0.76 | -0.77 | -0.78 | -0.79 | -0.8 | -0.8 | -0.81 | -0.81 | -0.81
| Water Efficient Appliance Subsidy | C026 | Ml/d | 2 | 0 | 0 | 0 | 0 | -0.03 | -0.06 | -0.09 | -0.1 | -0.1 | -0.11 | -0.12 | -0.13 | -0.14 | -0.15 | -0.15 | -0.16 | -0.17 | -0.17 | -0.18 | -0.18 | -0.18 | -0.18 | -0.19 | -0.19 | -0.19 | -0.19 | -0.19 | -0.19 | -0.19
| Waterwise Programme | C046 | Ml/d | 2 | 0 | 0 | 0 | 0 | -0.07 | -0.09 | -0.13 | -0.22 | -0.49 | -0.52 | -0.59 | -0.65 | -0.7 | -0.75 | -0.8 | -0.84 | -0.89 | -0.92 | -0.96 | -1 | -1.03 | -1.06 | -1.09 | -1.11 | -1.14 | -1.16 | -1.18 | -1.2 | -1.22
| Metering on change of occupancy - all properties | C006b | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.45 | 6.65 | 9.63 | 12.39 | 14.96 | 17.35 | 19.56 | 21.61 | 23.52 | 25.28 | 26.92 | 28.43 | 29.83 | 31.13 | 32.32 | 33.43 | 34.45 | 35.39 | 36.26 | 37.05
| Metering on change of occupancy - existing meter pits | C006a | Ml/d | 2 | 0 | 0 | 0 | 0 | 0.87 | 1.78 | 2.73 | 3.71 | 4.73 | 4.73 | 4.73 | 4.73 | 4.73 | 4.73 | 4.73 | 4.73 | 4.73 | 4.73 | 4.73 | 4.73 | 4.73 | 4.73 | 4.73 | 4.73 | 4.73 | 4.73 | 4.73 | 4.73 | 4.73
| Smart Metering Trial (NFR ) | C005 | Ml/d | 2 | 0 | 0 | 0.02 | 0.04 | 0.06 | 0.08 | 0.1 | 0.12 | 0.15 | 0.17 | 0.19 | 0.21 | 0.23 | 0.25 | 0.27 | 0.29 | 0.31 | 0.33 | 0.35 | 0.37 | 0.39 | 0.41 | 0.44 | 0.46 | 0.48 | 0.5 | 0.52 | 0.54 | 0.56
| Void Household Metering | C084 | Ml/d | 2 | 0 | 0 | 0 | 0 | 0.08 | 0.16 | 0.24 | 0.32 | 0.4 | 0.47 | 0.55 | 0.63 | 0.71 | 0.79 | 0.87 | 0.95 | 1.03 | 1.11 | 1.19 | 1.26 | 1.34 | 1.42 | 1.5 | 1.58 | 1.66 | 1.74 | 1.82 | 1.9 | 1.98
| Calls for Restraint | C078 | Ml/d | 2 | -0.79 | -0.79 | -0.84 | -0.89 | -0.99 | -1.07 | -1.15 | -1.23 | -1.31 | -1.48 | -1.64 | -1.79 | -1.94 | -2.07 | -2.2 | -2.33 | -2.44 | -2.56 | -2.66 | -2.77 | -2.86 | -2.95 | -3.04 | -3.12 | -3.19 | -3.26 | -3.33 | -3.39 | -3.45
| Hosepipe Ban | C079 | Ml/d | 2 | -1.53 | -1.53 | -1.64 | -1.74 | -1.93 | -2.08 | -2.24 | -2.39 | -2.56 | -2.88 | -3.19 | -3.49 | -3.77 | -4.04 | -4.29 | -4.54 | -4.76 | -4.99 | -5.2 | -5.39 | -5.58 | -5.75 | -5.92 | -6.08 | -6.23 | -6.37 | -6.5 | -6.62 | -6.73
| Volume Reallocation: Climate Change, Baseline Water Efficiency, Occupancy ineficiency | N/A | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | -0.01 | -0.06 | -0.06 | -0.11 | -0.15 | -0.21 | -0.33 | -0.48 | -0.59 | -0.74 | -0.86 | -0.96 | -1.1 | -1.22 | -1.32 | -1.43 | -1.54 | -1.65 | -1.76 | -1.87 | -1.97 | -2.08 | -2.19 | -2.28
- | (insert row above) | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: 2032-33 to 2044-45
61.4 | Change volume delivered to unmeasured households (input reductions as -ve) | - | Ml/d | 2 | -10.24 | -10.24 | -10.1 | -9.9683 | -11.3208 | -12.5729 | -13.8874 | -15.2112 | -16.8505 | -20.3529 | -23.4856 | -26.4198 | -29.1353 | -31.672 | -34.0296 | -36.2083 | -38.2177 | -40.088 | -41.7991 | -43.4008 | -44.9132 | -46.2662 | -47.5298 | -48.7039 | -49.7785 | -50.7635 | -51.6889 | -52.5547 | -53.3274
- | Retrofit Existing Toilets | C034 | Ml/d | 2 | 0 | 0 | 0 | 0 | -0.03 | -0.05 | -0.08 | -0.07 | -0.07 | -0.07 | -0.06 | -0.06 | -0.05 | -0.05 | -0.04 | -0.04 | -0.04 | -0.03 | -0.03 | -0.03 | -0.03 | -0.02 | -0.02 | -0.02 | -0.02 | -0.02 | -0.02 | -0.01 | -0.01
| Instal spray Taps | C040 | Ml/d | 2 | 0 | 0 | 0 | 0 | -0.01 | -0.02 | -0.03 | -0.04 | -0.05 | -0.05 | -0.04 | -0.04 | -0.04 | -0.03 | -0.03 | -0.03 | -0.03 | -0.02 | -0.02 | -0.02 | -0.02 | -0.02 | -0.02 | -0.01 | -0.01 | -0.01 | -0.01 | -0.01 | -0.01
| Trigger nozzles & water butts | C043 | Ml/d | 1 | 0 | 0 | 0 | 0 | 0 | -0.015207 | -0.029277 | -0.042282 | -0.040412 | -0.038609 | -0.035414 | -0.032534 | -0.029922 | -0.027508 | -0.025285 | -0.023231 | -0.021336 | -0.019578 | -0.017963 | -0.016472 | -0.015102 | -0.013836 | -0.012675 | -0.011604 | -0.010623 | -0.0097183 | -0.0088912 | -0.0081283 | -0.0074321
| Household Water Efficiency Programme | C046 | Ml/d | 2 | 0 | 0 | 0 | 0 | -0.19 | -0.37 | -0.54 | -0.69 | -0.83 | -0.8 | -0.73 | -0.67 | -0.62 | -0.57 | -0.52 | -0.48 | -0.44 | -0.4 | -0.37 | -0.34 | -0.31 | -0.29 | -0.26 | -0.24 | -0.22 | -0.2 | -0.18 | -0.17 | -0.15
| Water Efficient Appliance Subsidy | C026 | Ml/d | 3 | 0 | 0 | 0 | -0.078327 | -0.15076 | -0.2177 | -0.20814 | -0.19894 | -0.19006 | -0.17433 | -0.16015 | -0.1473 | -0.13541 | -0.12447 | -0.11436 | -0.10503 | -0.096379 | -0.088426 | -0.081088 | -0.074343 | -0.06811 | -0.062397 | -0.057123 | -0.052294 | -0.04784 | -0.043769 | -0.040013 | -0.036586 | 0
| Waterwise Programme | C046b | Ml/d | 2 | 0 | 0 | 0 | 0 | -0.21 | -0.24 | -0.31 | -0.47 | -0.95 | -0.92 | -0.85 | -0.79 | -0.74 | -0.69 | -0.65 | -0.6 | -0.56 | -0.52 | -0.49 | -0.45 | -0.42 | -0.39 | -0.36 | -0.34 | -0.31 | -0.29 | -0.27 | -0.25 | -0.23
| Metering on change of occupancy - all properties | C006b | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -4.05 | -7.82 | -11.33 | -14.58 | -17.6 | -20.41 | -23.01 | -25.43 | -27.67 | -29.74 | -31.67 | -33.45 | -35.1 | -36.62 | -38.03 | -39.33 | -40.53 | -41.64 | -42.65 | -43.59
| Metering on change of occupancy - existing meter pits | C006a | Ml/d | 2 | 0 | 0 | 0 | 0 | -1.02 | -2.1 | -3.21 | -4.37 | -5.56 | -5.56 | -5.56 | -5.56 | -5.56 | -5.56 | -5.56 | -5.56 | -5.56 | -5.56 | -5.56 | -5.56 | -5.56 | -5.56 | -5.56 | -5.56 | -5.56 | -5.56 | -5.56 | -5.56 | -5.56
| Smart Metering Trial (NFR ) | C005 | Ml/d | 2 | 0 | 0 | -0.02 | -0.05 | -0.07 | -0.1 | -0.12 | -0.15 | -0.17 | -0.2 | -0.22 | -0.24 | -0.27 | -0.29 | -0.32 | -0.34 | -0.37 | -0.39 | -0.41 | -0.44 | -0.46 | -0.49 | -0.51 | -0.54 | -0.56 | -0.59 | -0.61 | -0.63 | -0.66
| Void Household Metering | C084 | Ml/d | 2 | 0 | 0 | 0 | 0 | -0.09 | -0.19 | -0.28 | -0.37 | -0.47 | -0.56 | -0.65 | -0.74 | -0.84 | -0.93 | -1.02 | -1.12 | -1.21 | -1.3 | -1.39 | -1.49 | -1.58 | -1.67 | -1.77 | -1.86 | -1.95 | -2.05 | -2.14 | -2.23 | -2.32
| Calls for Restraint | C078 | Ml/d | 2 | -3.47 | -3.47 | -3.41 | -3.36 | -3.27 | -3.19 | -3.11 | -3.03 | -2.94 | -2.78 | -2.62 | -2.47 | -2.32 | -2.18 | -2.05 | -1.93 | -1.81 | -1.7 | -1.59 | -1.49 | -1.4 | -1.31 | -1.22 | -1.14 | -1.06 | -0.99 | -0.92 | -0.86 | -0.8
| Hosepipe Ban | C079 | Ml/d | 2 | -6.77 | -6.77 | -6.66 | -6.56 | -6.37 | -6.22 | -6.06 | -5.91 | -5.74 | -5.42 | -5.11 | -4.81 | -4.53 | -4.26 | -4.01 | -3.77 | -3.54 | -3.31 | -3.1 | -2.91 | -2.72 | -2.55 | -2.38 | -2.22 | -2.07 | -1.93 | -1.8 | -1.68 | -1.57
| Volume Reallocation: Climate Change, Baseline Water Efficiency, Occupancy ineficiency | N/A | Ml/d | 2 | 0 | 0 | -0.01 | 0.08 | 0.09 | 0.14 | 0.09 | 0.13 | 0.16 | 0.27 | 0.37 | 0.47 | 0.58 | 0.64 | 0.72 | 0.8 | 0.89 | 0.92 | 1 | 1.09 | 1.12 | 1.21 | 1.26 | 1.32 | 1.37 | 1.46 | 1.51 | 1.54 | 1.58
- | (insert row above) | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: 2032-33 to 2044-45
61.5 | Options to reduce water taken unbilled (input as -ve) | - | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- |  |  | Ml/d | 2
- | (insert row above) | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: 2032-33 to 2044-45
61.6 | Options impacting on measured Non Household - USPL (input reductions as -ve) |  | l/pr | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- |  |  | Ml/d | 2
- | (insert row above) | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: 2032-33 to 2044-45
61.7 | Options impacting on unmeasured Non Household - USPL (input reductions as -ve) |  | l/pr | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- |  |  | Ml/d | 2
- | (insert row above) | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: 2032-33 to 2044-45
61.8 | Options impacting on measured Household - USPL (input reductions as -ve) |  | l/pr | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.06 | 0.09 | 0.12 | 0.16 | 0.27 | 0.37 | 0.46 | 0.56 | 0.63 | 0.71 | 0.77 | 0.85 | 0.9 | 0.96 | 1.01 | 1.06 | 1.11 | 1.15 | 1.18 | 1.23 | 1.27 | 1.3
- | Smart Metering Trial (NFR ) | C005 | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.02 | 0.02
| Metering on change of occupancy - existing meter pits | C006a | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.03 | 0.05 | 0.08 | 0.11 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14 | 0.14
| Metering on change of occupancy - all properties | C006b | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.1 | 0.2 | 0.29 | 0.38 | 0.45 | 0.53 | 0.59 | 0.66 | 0.71 | 0.77 | 0.82 | 0.86 | 0.91 | 0.95 | 0.98 | 1.02 | 1.05 | 1.08
| Void Household Metering | C084 | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0.01 | 0.01 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03 | 0.03 | 0.03 | 0.03 | 0.04 | 0.04 | 0.04 | 0.04 | 0.05 | 0.05 | 0.05 | 0.05 | 0.06 | 0.06 | 0.06
- | (insert row above) | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: 2032-33 to 2044-45
61.9 | Options impacting on unmeasured Household - USPL (input reductions as -ve) |  | l/pr | 2 | 0 | 0 | 0 | 0 | -0.03 | -0.07 | -0.1 | -0.14 | -0.18 | -0.29 | -0.39 | -0.5 | -0.59 | -0.67 | -0.75 | -0.83 | -0.9 | -0.96 | -1.03 | -1.09 | -1.13 | -1.2 | -1.24 | -1.28 | -1.32 | -1.37 | -1.4 | -1.43 | -1.47
- | Smart Metering Trial (NFR ) | C005 | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -0.1 | -0.2 | -0.29 | -0.38 | -0.45 | -0.53 | -0.59 | -0.66 | -0.71 | -0.77 | -0.82 | -0.86 | -0.91 | -0.95 | -0.98 | -1.02 | -1.05 | -1.08 | -1.1 | -1.13
| Metering on change of occupancy - existing meter pits | C006a | Ml/d | 2 | 0 | 0 | 0 | 0 | -0.03 | -0.05 | -0.08 | -0.11 | -0.14 | -0.14 | -0.14 | -0.14 | -0.14 | -0.14 | -0.14 | -0.14 | -0.14 | -0.14 | -0.14 | -0.14 | -0.14 | -0.14 | -0.14 | -0.14 | -0.14 | -0.14 | -0.14 | -0.14 | -0.14
| Metering on change of occupancy - all properties | C006b | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | -0.01 | -0.01 | -0.01 | -0.02 | -0.02 | -0.02 | -0.03 | -0.03 | -0.03 | -0.03 | -0.04 | -0.04 | -0.04 | -0.05 | -0.05 | -0.05 | -0.06 | -0.06 | -0.06 | -0.06 | -0.07 | -0.07 | -0.07 | -0.08
| Void Household Metering | C084 | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | -0.01 | -0.01 | -0.02 | -0.02 | -0.03 | -0.03 | -0.04 | -0.04 | -0.05 | -0.05 | -0.06 | -0.06 | -0.07 | -0.07 | -0.08 | -0.08 | -0.09 | -0.09 | -0.1 | -0.1 | -0.11 | -0.11 | -0.12 | -0.12
- | (insert row above) | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: 2032-33 to 2044-45
61.1 | Options impacting on Void properties - USPL (input reductions as -ve) |  | l/pr | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- |  |  | Ml/d | 2
- | (insert row above) | - | - |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: 2032-33 to 2044-45
| Company: | Portsmouth Water
| Resource Zone Name: | Company
| Resource Zone Number: | PRT 1
| Planning Scenario Name: | Dry Year Annual Average - benchmarking data
| Chosen Level of Service: | 1 in 200

## 7. FP Supply
Table 7: Final planning water supply
| Row Ref | Component | Derivation | Unit | Decimal places | 2017/18 | For info 2017-18 | For info 2018-19 | For info 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-2030 | 2030-2031 | 2031-2032 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
Resources | 1FP | Raw Water Abstracted | 1BL | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 2FP | Raw Water Imported | 2BL+ (6. Preferred scenario ref 58.2) | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| - | - | - | - | 2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: 2032-33 to 2044-45
| - | - | - | - | 2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: 2032-33 to 2044-45
| - | - | - | - | 2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: 2032-33 to 2044-45
| 3FP | Potable Water Imported | 3BL+ (6. Preferred scenario ref 58.3) | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| - | - | - | - | 2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: 2032-33 to 2044-45
| - | - | - | - | 2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: 2032-33 to 2044-45
| - | - | - | - | 2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: 2032-33 to 2044-45
| - | - | - | - | 2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: 2032-33 to 2044-45
Resource (and process) losses | 5FP | Raw Water Exported (raw exports and non potable uses) | 5BL+ (6. Preferred scenario ref 58.5) | Ml/d | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| - | - | - | - | 2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: 2032-33 to 2044-45
| - | - | - | - | 2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: 2032-33 to 2044-45
| - | - | - | - | 2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: 2032-33 to 2044-45
| 6FP | Potable Water Exported | 6BL+ (6. Preferred scenario ref 58.6) | Ml/d | 2 | 15 | 15 | 15 | 22.5 | 30 | 30 | 30 | 30 | 39 | 39 | 39 | 39 | 39 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60 | 60
| - | - | - | - | 2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: 2032-33 to 2044-45
| - | - | - | - | 2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: 2032-33 to 2044-45
| - | - | - | - | 2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: 2032-33 to 2044-45
| 7FP | Deployable Output | 7BL+ 8BL+ (6. Preferred scenario ref 58.7) + (6. Preferred scenario ref 58.1) |  | 2 | 199.2 | 199.2 | 199.2 | 206.93 | 206.8945 | 206.859 | 206.8235 | 206.788 | 219.2525 | 219.217 | 219.1815 | 219.146 | 219.1105 | 242.075 | 242.0395 | 242.004 | 241.9685 | 241.933 | 241.8975 | 241.862 | 241.8265 | 241.791 | 241.7555 | 241.72 | 241.6845 | 241.649 | 241.6135 | 241.578 | 241.5425
| - | - | - | - | 2 |  |  |  |  | - | - | - | - | - | - | - | - | - | - | - | - | bar: 2032-33 to 2044-45
| - | - | - | - | 2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: 2032-33 to 2044-45
| - | - | - | - | 2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: 2032-33 to 2044-45
| - | - | - | - | 2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: 2032-33 to 2044-45
| - | - | - | - | 2 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: 2032-33 to 2044-45
| 9FP | Raw water losses, treatment works losses and operational use | 9BL+ (6. Preferred scenario ref 60.1)+(6. Preferred scenario ref 58.4) | Ml/d | 2 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4 | 2.4
| 10FP | Outage allowance | 10BL+ (6. Preferred scenario ref 60.2) | Ml/d | 2 | 12.96 | 12.96 | 12.96 | 13.05 | 13.05 | 13.05 | 13.05 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 13.5 | 14.64 | 14.64 | 14.64 | 14.64 | 14.64 | 14.64 | 14.64 | 14.64 | 14.64 | 14.64 | 14.64 | 14.64 | 14.64 | 14.64 | 14.64 | 14.64
|  | Company: | Portsmouth Water
|  | Resource Zone Name: | Company
|  | Resource Zone Number: | PRT 1
|  | Planning Scenario Name: | Dry Year Annual Average - benchmarking data
|  | Chosen Level of Service: | 1 in 200
Note on E3: Author: 58.1 has been added into 7FP Deployable Ouput calculations to ensure that it is reflected in final supply-demand balance calculations. Please ensure that you do not double count increases to raw water abstractions and increases to deployable output

## 8. FP Demand
Table 8: Final planning water demand
| Row Ref | Component | Derivation / Impact of preferred options | Unit | Decimal places | 2017/18 | For info 2017-18 | For info 2018-19 | For info 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-2030 | 2030-2031 | 2031-2032 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
Consumption | 19FP | Water Delivered Measured Non Household | Calculated BL+Preferred options | Ml/d | 2 | 25.38 | 25.38 | 25.21 | 25.02 | 24.83 | 24.64 | 24.45 | 24.26 | 24.08 | 23.89 | 23.7 | 23.51 | 23.32 | 23.14 | 22.95 | 22.76 | 22.57 | 22.38 | 22.19 | 22 | 21.83 | 21.69 | 21.54 | 21.4 | 21.25 | 21.1 | 20.96 | 20.81 | 20.67
| 20FP | Water Delivered Unmeasured Non Household | Calculated BL+Preferred options | Ml/d | 2 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
| 21FP | Water Delivered Measured Household | Calculated BL+Preferred options | Ml/d | 2 | 22.53 | 22.53 | 24.07 | 25.68 | 27.8346 | 29.9883 | 32.0712 | 34.1002 | 35.8692 | 40.0982 | 43.9159 | 47.5039 | 50.8321 | 53.9605 | 56.8791 | 59.6079 | 62.2467 | 64.6858 | 67.0049 | 69.1842 | 71.2535 | 73.223 | 75.0625 | 76.8122 | 78.4819 | 80.0717 | 81.5715 | 83.0214 | 84.3914
| 22FP | Water Delivered Unmeasured Household | Calculated BL+Preferred options | Ml/d | 2 | 74.94 | 74.94 | 74.09 | 73.4417 | 71.2492 | 69.1971 | 67.1326 | 65.0788 | 62.7595 | 58.5271 | 54.7044 | 51.1302 | 47.8147 | 44.718 | 41.8304 | 39.1517 | 36.6723 | 34.362 | 32.2209 | 30.2092 | 28.3368 | 26.6038 | 25.0002 | 23.4961 | 22.1115 | 20.8165 | 19.6111 | 18.4753 | 17.4326
| 23FP | Measured Non Household - Consumption | 19FP-34FP | Ml/d | 2 | 25.1 | 25.1 | 24.93 | 24.74 | 24.56 | 24.37 | 24.19 | 24 | 23.83 | 23.64 | 23.45 | 23.27 | 23.08 | 22.9 | 22.71 | 22.53 | 22.34 | 22.15 | 21.96 | 21.78 | 21.61 | 21.47 | 21.32 | 21.18 | 21.04 | 20.89 | 20.75 | 20.6 | 20.46
| 24FP | Unmeasured Non Household - Consumption | 20FP-35FP | Ml/d | 2 | 0.85 | 0.85 | 0.86 | 0.86 | 0.86 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87 | 0.87
| 25FP | Measured Household - Consumption | 21FP-36FP | Ml/d | 2 | 20.74 | 20.74 | 22.28 | 23.89 | 25.9946 | 28.0883 | 30.0412 | 31.9702 | 33.6292 | 37.7482 | 41.4459 | 44.7739 | 47.8621 | 50.7705 | 53.4591 | 56.0079 | 58.4567 | 60.7358 | 62.8749 | 64.9142 | 66.8335 | 68.673 | 70.3825 | 72.0122 | 73.5719 | 75.0617 | 76.4415 | 77.7914 | 79.0714
| 26FP | Unmeasured Household - Consumption | 22FP-37FP | Ml/d | 2 | 68.82 | 68.82 | 67.99 | 67.3617 | 65.2192 | 63.2271 | 61.2126 | 59.2188 | 56.9495 | 52.8471 | 49.1344 | 45.6802 | 42.4747 | 39.468 | 36.6704 | 34.0817 | 31.6823 | 29.442 | 27.3809 | 25.4392 | 23.6168 | 21.9538 | 20.4002 | 18.9461 | 17.6115 | 16.3665 | 15.2011 | 14.0953 | 13.1026
| 27 - | Percentage of consumption driven by climate change | n/a in FP | - | 1 | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: 2032-33 to 2044-45
| 28 - | Volume of consumption driven by climate change | n/a in FP | - | 1 |  | - | - | - | - | - | - | - | - | - | - | - | - | - | - | - | bar: 2032-33 to 2044-45
PCC and consumption by component | 29FP | Measured Household - PCC | (25FP*1,000,000)/(51FP*1,000) | l/h/d | 1 | 120 | 120 | 120 | 121 | 119 | 118 | 117 | 116 | 115 | 114 | 114 | 113 | 112 | 112 | 111 | 111 | 111 | 111 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110 | 110
| 29.1FP | Measured toilet flushing | Input brief explanation here | l/h/d | 1 | 29.7 | 29.7 | 29.7 | 29.8 | 29.1 | 28.7 | 28.3 | 27.9 | 27.4 | 27.1 | 26.9 | 26.5 | 26 | 25.9 | 25.5 | 25.2 | 25.1 | 24.9 | 24.5 | 24.4 | 24.2 | 24 | 23.9 | 23.7 | 23.5 | 23.3 | 23.2 | 23 | 22.8
| 29.2FP | Measured personal washing | Input brief explanation here | l/h/d | 1 | 53.6 | 53.6 | 53.9 | 54.5 | 53.7 | 53.5 | 53.2 | 52.9 | 52.6 | 52.4 | 52.5 | 52.2 | 52 | 52.1 | 51.8 | 52 | 52.1 | 52.3 | 52 | 52.2 | 52.4 | 52.5 | 52.7 | 52.9 | 53.1 | 53.3 | 53.4 | 53.7 | 53.9
| 29.3FP | Measured clothes washing | Input brief explanation here | l/h/d | 1 | 17.4 | 17.4 | 17.3 | 17.4 | 17.2 | 17.1 | 16.9 | 16.8 | 16.6 | 16.5 | 16.5 | 16.4 | 16.2 | 16.3 | 16.1 | 16.1 | 16.1 | 16.1 | 16 | 16 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9 | 15.9
| 29.4FP | Measured dish washing | Input brief explanation here | l/h/d | 1 | 11 | 11 | 10.8 | 11 | 10.8 | 10.7 | 10.6 | 10.5 | 10.4 | 10.3 | 10.3 | 10.2 | 10.2 | 10.1 | 10.1 | 10.1 | 10.1 | 10.1 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9 | 9.9
| 29.5FP | Measured miscellaneous internal use | Input brief explanation here | l/h/d | 1 | 7.9 | 7.9 | 7.8 | 7.9 | 7.8 | 7.7 | 7.6 | 7.6 | 7.5 | 7.4 | 7.4 | 7.3 | 7.3 | 7.3 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.2 | 7.1 | 7.1
| 29.6FP | Measured external use | Input brief explanation here | l/h/d | 1 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4 | 0.4
| 30FP | Unmeasured Household - PCC | (26FP*1,000,000)/(52FP*1,000) | l/h/d | 1 | 128 | 128 | 128 | 128 | 127 | 127 | 127 | 126 | 125 | 125 | 125 | 125 | 125 | 126 | 126 | 126 | 127 | 127 | 128 | 129 | 129 | 130 | 131 | 132 | 133 | 134 | 136 | 137 | 138
| 30.1FP | Unmeasured toilet flushing | Input brief explanation here | l/h/d | 1 | 38.9 | 38.9 | 39 | 38.9 | 38.4 | 38.3 | 38.2 | 37.8 | 37.3 | 37.1 | 37 | 36.8 | 36.7 | 36.9 | 36.7 | 36.5 | 36.7 | 36.5 | 36.7 | 36.7 | 36.6 | 36.8 | 36.9 | 37 | 37.1 | 37.2 | 37.6 | 37.8 | 37.8
| 30.2FP | Unmeasured personal washing | Input brief explanation here | l/h/d | 1 | 47.3 | 47.3 | 47.2 | 47.2 | 46.9 | 46.9 | 46.9 | 46.5 | 46.2 | 46.2 | 46.2 | 46.2 | 46.3 | 46.7 | 46.7 | 46.7 | 47.1 | 47.3 | 47.6 | 48 | 48.1 | 48.5 | 48.9 | 49.3 | 49.8 | 50.2 | 50.9 | 51.4 | 51.9
| 30.3FP | Unmeasured clothes washing | Input brief explanation here | l/h/d | 1 | 17.6 | 17.6 | 17.6 | 17.7 | 17.6 | 17.6 | 17.7 | 17.6 | 17.6 | 17.6 | 17.7 | 17.8 | 17.8 | 18 | 18.1 | 18.1 | 18.3 | 18.3 | 18.5 | 18.8 | 18.8 | 19 | 19.2 | 19.4 | 19.6 | 19.8 | 20.1 | 20.3 | 20.5
| 30.4FP | Unmeasured dish washing | Input brief explanation here | l/h/d | 1 | 13.2 | 13.2 | 13.2 | 13.1 | 13.1 | 13.1 | 13.2 | 13.1 | 13 | 13.1 | 13.2 | 13.1 | 13.2 | 13.3 | 13.3 | 13.4 | 13.5 | 13.5 | 13.7 | 13.9 | 13.9 | 14 | 14.2 | 14.3 | 14.4 | 14.6 | 14.9 | 15 | 15.1
| 30.5FP | Unmeasured miscellaneous internal use | Input brief explanation here | l/h/d | 1 | 9.2 | 9.2 | 9.1 | 9.2 | 9.1 | 9.1 | 9.2 | 9.1 | 9.1 | 9.1 | 9.1 | 9.2 | 9.1 | 9.2 | 9.3 | 9.3 | 9.4 | 9.4 | 9.5 | 9.6 | 9.6 | 9.7 | 9.8 | 10 | 10 | 10.1 | 10.3 | 10.4 | 10.5
| 30.6FP | Unmeasured external use | Input brief explanation here | l/h/d | 1 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 1.9 | 2 | 2 | 2 | 2 | 2 | 2 | 2.1 | 2.1 | 2.1 | 2.2 | 2.2
| 31FP | Average Household - PCC | ((25FP+26FP)*1,000,000))/(51FP+52FP*1,000) | l/h/d | 1 | 125.7124 | 125.7124 | 125.6997 | 126.0382 | 125.019 | 124.2911 | 123.3443 | 122.4342 | 120.8667 | 120.1609 | 119.5196 | 118.7825 | 118.0765 | 117.4583 | 116.8555 | 116.3587 | 115.9792 | 115.5858 | 115.2575 | 114.9475 | 114.6348 | 114.4277 | 114.1792 | 113.9457 | 113.8071 | 113.6756 | 113.5076 | 113.3732 | 113.2901
| 32FP | Water Taken Unbilled | Calculated BL+Preferred options | Ml/d | 1 | 2.45 | 2.45 | 2.4499 | 2.4499 | 2.4499 | 2.4499 | 2.4499 | 2.4499 | 2.4499 | 2.4499 | 2.4499 | 2.4499 | 2.4499 | 2.4499 | 2.4499 | 2.4499 | 2.4499 | 2.4499 | 2.4499 | 2.4499 | 2.4499 | 2.4499 | 2.4499 | 2.4499 | 2.4499 | 2.4499 | 2.4499 | 2.4499 | 2.4499
| 33FP | Distribution System Operational Use | Calculated BL+Preferred options | Ml/d | 1 | 0.43 | 0.43 | 0.42897 | 0.42897 | 0.42897 | 0.42897 | 0.42897 | 0.42897 | 0.42897 | 0.42897 | 0.42897 | 0.42897 | 0.42897 | 0.42897 | 0.42897 | 0.42897 | 0.42897 | 0.42897 | 0.42897 | 0.42897 | 0.42897 | 0.42897 | 0.42897 | 0.42897 | 0.42897 | 0.42897 | 0.42897 | 0.42897 | 0.42897
Leakage | 34FP | Measured Non Household - USPL | Calculated BL+Preferred options | Ml/d | 2 | 0.28 | 0.28 | 0.28 | 0.28 | 0.27 | 0.27 | 0.26 | 0.26 | 0.25 | 0.25 | 0.25 | 0.24 | 0.24 | 0.24 | 0.24 | 0.23 | 0.23 | 0.23 | 0.23 | 0.22 | 0.22 | 0.22 | 0.22 | 0.22 | 0.21 | 0.21 | 0.21 | 0.21 | 0.21
| 35FP | Unmeasured Non Household - USPL | Calculated BL+Preferred options | Ml/d | 2 | 0.05 | 0.05 | 0.04 | 0.04 | 0.04 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
| 36FP | Measured Household - USPL | Calculated BL+Preferred options | Ml/d | 2 | 1.79 | 1.79 | 1.79 | 1.79 | 1.84 | 1.9 | 2.03 | 2.13 | 2.24 | 2.35 | 2.47 | 2.73 | 2.97 | 3.19 | 3.42 | 3.6 | 3.79 | 3.95 | 4.13 | 4.27 | 4.42 | 4.55 | 4.68 | 4.8 | 4.91 | 5.01 | 5.13 | 5.23 | 5.32
| 37FP | Unmeasured Household - USPL | Calculated BL+Preferred options | Ml/d | 2 | 6.12 | 6.12 | 6.1 | 6.08 | 6.03 | 5.97 | 5.92 | 5.86 | 5.81 | 5.68 | 5.57 | 5.45 | 5.34 | 5.25 | 5.16 | 5.07 | 4.99 | 4.92 | 4.84 | 4.77 | 4.72 | 4.65 | 4.6 | 4.55 | 4.5 | 4.45 | 4.41 | 4.38 | 4.33
| 38FP | Void Properties - USPL | Calculated BL+Preferred options | Ml/d | 2 | 0.28 | 0.28 | 0.27 | 0.28 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27 | 0.27
| 39FP | Distribution Losses | Calculated BL+Preferred options | Ml/d | 2 | 26.52 | 26.52 | 26.47 | 26.4 | 25.05 | 23.66 | 22.19 | 20.75 | 19.3 | 19.06 | 18.79 | 18.4 | 18.01 | 17.62 | 17.22 | 16.88 | 16.51 | 16.16 | 15.8 | 15.48 | 15.12 | 14.8 | 14.46 | 14.13 | 13.82 | 13.51 | 13.17 | 12.84 | 12.54
| 40FP | Total Leakage | Sum(34FP:39FP) | Ml/d | 2 | 35.04 | 35.04 | 34.95 | 34.87 | 33.5 | 32.1 | 30.7 | 29.3 | 27.9 | 27.64 | 27.38 | 27.12 | 26.86 | 26.6 | 26.34 | 26.08 | 25.82 | 25.56 | 25.3 | 25.04 | 24.78 | 24.52 | 24.26 | 24 | 23.74 | 23.48 | 23.22 | 22.96 | 22.7
| 41FP | Total Leakage | (40FP*1,000,000)/(48FP*1,000) | l/prop/d | 2 | 109.6302 | 109.6302 | 108.1943 | 106.7275 | 101.5244 | 96.3906 | 91.3881 | 86.5098 | 81.7463 | 80.3979 | 79.1375 | 77.8975 | 76.699 | 75.5274 | 74.3879 | 73.2584 | 72.1209 | 70.998 | 69.8992 | 68.8082 | 67.729 | 66.6522 | 65.5942 | 64.5404 | 63.5031 | 62.4751 | 61.453 | 60.4433 | 59.4443
Customer: Properties | 42FP | Measured Non Household - Properties | Input (total, excluding voids) | 000's | 2 | 13.82 | 13.82 | 13.95 | 13.82 | 13.57 | 13.33 | 13.12 | 12.91 | 12.71 | 12.53 | 12.35 | 12.19 | 12.04 | 11.9 | 11.76 | 11.63 | 11.51 | 11.39 | 11.28 | 11.17 | 11.06 | 10.96 | 10.86 | 10.77 | 10.68 | 10.59 | 10.51 | 10.44 | 10.37
| 43FP | Unmeasured Non Household - Properties | Input (total, excluding voids) | 000's | 2 | 1.81 | 1.81 | 1.81 | 1.81 | 1.77 | 1.74 | 1.72 | 1.69 | 1.66 | 1.64 | 1.62 | 1.59 | 1.57 | 1.56 | 1.54 | 1.52 | 1.5 | 1.49 | 1.47 | 1.46 | 1.45 | 1.43 | 1.42 | 1.41 | 1.4 | 1.39 | 1.38 | 1.37 | 1.36
| 44FP | All void non-households - properties | Input (voids in each year) | 000's | 2 | 3.62 | 3.62 | 3.62 | 3.62 | 3.54 | 3.53 | 3.48 | 3.43 | 3.38 | 3.34 | 3.29 | 3.26 | 3.22 | 3.19 | 3.15 | 3.12 | 3.08 | 3.05 | 3.02 | 2.99 | 2.96 | 2.94 | 2.91 | 2.89 | 2.86 | 2.84 | 2.82 | 2.8 | 2.78
| 45FP | Measured Household - Properties (excl voids) | Pre-plan year = input. Forecast years = Previous year 45FP + sum(45.1FP:45.6FP) | 000's | 2 | 89.29 | 89.29 | 95.09 | 100.99 | 109.57 | 117.86 | 126.03 | 134.05 | 141.91 | 156.93 | 170.87 | 183.98 | 196.26 | 207.77 | 218.57 | 228.78 | 238.54 | 247.75 | 256.44 | 264.68 | 272.53 | 279.99 | 287.08 | 293.83 | 300.26 | 306.4 | 312.26 | 317.86 | 323.22
| 45.1FP | New properties | Input (new builds in each year) | 000's | 2 | 0 | 0 | 3.42 | 3.66 | 3.58 | 3.29 | 3.17 | 3.02 | 2.86 | 2.73 | 2.48 | 2.41 | 2.3 | 2.19 | 2.11 | 2.1 | 2.2 | 2.16 | 2.12 | 2.11 | 2.13 | 2.12 | 2.11 | 2.11 | 2.11 | 2.11 | 2.1 | 2.1 | 2.1
| 45.2FP | Meter optants - properties | Input (meter optants in each year) | 000's | 2 | 0 | 0 | 2.32 | 2.18 | 2.05 | 1.93 | 1.82 | 1.71 | 1.61 | 1.52 | 1.43 | 1.35 | 1.28 | 1.21 | 1.14 | 1.08 | 1.02 | 0.96 | 0.91 | 0.86 | 0.82 | 0.78 | 0.74 | 0.7 | 0.66 | 0.63 | 0.6 | 0.57 | 0.54
| 45.3FP | Compulsory metering - properties | Input (compulsory meters in each year) | 000's | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 45.4FP | Metering on change of occupancy - properties | Input (change of occupancy meters in each year) | 000's | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.47 | 9.73 | 9.05 | 8.4 | 7.81 | 7.25 | 6.73 | 6.24 | 5.79 | 5.36 | 4.97 | 4.6 | 4.26 | 3.94 | 3.64 | 3.36 | 3.1 | 2.86 | 2.63 | 2.42
| 45.5FP | Selective metering properties | Input (selective meters in each year) | 000's | 2 | 0 | 0 | 0 | 0 | 2.65 | 2.77 | 2.88 | 2.99 | 3.09 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 45.6FP | Other changes to existing metering - properties | Input (other changes to meters in each year) | 000's | 2 | 0 | 0 | 0.06 | 0.06 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
| 45.7FP | Measured void households - properties | Input (voids in each year) | 000's | 2 | 1.49 | 1.49 | 1.74 | 1.88 | 2.04 | 2.2 | 2.35 | 2.5 | 2.65 | 2.95 | 3.21 | 3.46 | 3.69 | 3.9 | 4.11 | 4.3 | 4.48 | 4.66 | 4.82 | 4.98 | 5.12 | 5.27 | 5.4 | 5.53 | 5.65 | 5.76 | 5.87 | 5.98 | 6.08
| 46FP | Unmeasured households - properties (excl void) | Input (total) | 000's | 2 | 204.16 | 204.16 | 201.78 | 199.53 | 194.53 | 189.53 | 184.53 | 179.53 | 174.53 | 162.24 | 150.77 | 140.07 | 130.08 | 120.77 | 112.08 | 103.98 | 96.42 | 89.37 | 82.79 | 76.66 | 70.93 | 65.6 | 60.62 | 55.99 | 51.66 | 47.63 | 43.88 | 40.37 | 37.11
| 47FP | Unmeasured void households - properties | Input (voids in each year) | 000's | 2 | 5.43 | 5.43 | 5.04 | 5.07 | 4.95 | 4.83 | 4.7 | 4.58 | 4.46 | 4.16 | 3.87 | 3.6 | 3.34 | 3.1 | 2.88 | 2.67 | 2.48 | 2.3 | 2.13 | 1.97 | 1.82 | 1.69 | 1.56 | 1.44 | 1.33 | 1.22 | 1.13 | 1.04 | 0.95
| 48FP | Total Resource Zone Properties (incl voids) | SUM(42FP:45FP)+45.7FP+46FP+47FP | 000's | 2 | 319.62 | 319.62 | 323.03 | 326.72 | 329.97 | 333.02 | 335.93 | 338.69 | 341.3 | 343.79 | 345.98 | 348.15 | 350.2 | 352.19 | 354.09 | 356 | 358.01 | 360.01 | 361.95 | 363.91 | 365.87 | 367.88 | 369.85 | 371.86 | 373.84 | 375.83 | 377.85 | 379.86 | 381.87
Customer: Population | 49FP | Measured Non Household - Population | Input (total) | 000's | 2 | 12.34 | 12.34 | 12.41 | 12.5 | 12.61 | 12.7 | 12.86 | 13.02 | 13.18 | 13.34 | 13.46 | 13.66 | 13.87 | 14.08 | 14.3 | 14.53 | 14.87 | 15.14 | 15.38 | 15.58 | 15.75 | 15.93 | 16.11 | 16.29 | 16.47 | 16.65 | 16.84 | 17.02 | 17.21
| 50FP | Unmeasured Non Household - Population | Input (total) | 000's | 2 | 1.61 | 1.61 | 1.62 | 1.63 | 1.65 | 1.66 | 1.68 | 1.7 | 1.72 | 1.74 | 1.76 | 1.78 | 1.81 | 1.84 | 1.87 | 1.9 | 1.94 | 1.98 | 2.01 | 2.04 | 2.06 | 2.08 | 2.11 | 2.13 | 2.15 | 2.18 | 2.2 | 2.23 | 2.25
| 51FP | Measured Household - Population | Input (total) | 000's | 2 | 172.76 | 172.76 | 185.5 | 198.22 | 217.96 | 237.09 | 256.02 | 274.66 | 292.93 | 330.05 | 364.39 | 396.45 | 426.41 | 454.27 | 480.28 | 504.65 | 527.62 | 549.19 | 569.4 | 588.47 | 606.45 | 623.38 | 639.44 | 654.67 | 668.88 | 682.42 | 695.24 | 707.41 | 718.96
| 52FP | Unmeasured Household - Population | Input (total) | 000's | 2 | 539.66 | 539.66 | 532.64 | 525.78 | 511.64 | 497.6 | 483.81 | 470.14 | 456.48 | 423.9 | 393.48 | 365.06 | 338.66 | 313.99 | 291.01 | 269.59 | 249.58 | 230.99 | 213.68 | 197.57 | 182.58 | 168.62 | 155.65 | 143.59 | 132.33 | 121.87 | 112.13 | 103.07 | 94.65
| 53FP | Total Resource Zone Population | 49FP+Sum(50FP:52FP) | 000's | 2 | 726.37 | 726.37 | 732.17 | 738.13 | 743.86 | 749.05 | 754.37 | 759.52 | 764.31 | 769.03 | 773.09 | 776.95 | 780.75 | 784.18 | 787.46 | 790.67 | 794.01 | 797.3 | 800.47 | 803.66 | 806.84 | 810.01 | 813.31 | 816.68 | 819.83 | 823.12 | 826.41 | 829.73 | 833.07
Occupancy | 54FP | Measured Household - Occupancy Rate (average) (excl voids) | 51FP/45FP | h/prop | 1 | 1.9348 | 1.9348 | 1.9508 | 1.9628 | 1.9892 | 2.0116 | 2.0314 | 2.0489 | 2.0642 | 2.1032 | 2.1326 | 2.1549 | 2.1727 | 2.1864 | 2.1974 | 2.2058 | 2.2119 | 2.2167 | 2.2204 | 2.2233 | 2.2253 | 2.2264 | 2.2274 | 2.2281 | 2.2277 | 2.2272 | 2.2265 | 2.2255 | 2.2244
| 55FP | Unmeasured Household - Occupancy Rate | 52BL/46BL | h/prop | 1 | 2.6433 | 2.6433 | 2.6397 | 2.6351 | 2.6301 | 2.6254 | 2.6219 | 2.6187 | 2.6155 | 2.6128 | 2.6098 | 2.6063 | 2.6035 | 2.5999 | 2.5964 | 2.5927 | 2.5885 | 2.5846 | 2.581 | 2.5772 | 2.5741 | 2.5704 | 2.5676 | 2.5646 | 2.5616 | 2.5587 | 2.5554 | 2.5531 | 2.5505
Metering | 56FP | Total Household Metering penetration (excl. voids) | 45FP/45FP+46FP | % | 0 | 30.43% | 30.43% | 32.03% | 33.61% | 36.03% | 38.34% | 40.58% | 42.75% | 44.85% | 49.17% | 53.12% | 56.78% | 60.14% | 63.24% | 66.1% | 68.75% | 71.21% | 73.49% | 75.59% | 77.54% | 79.35% | 81.02% | 82.57% | 83.99% | 85.32% | 86.55% | 87.68% | 88.73% | 89.7%
| 57FP | Total Household Metering penetration (incl. voids) | 45FP/(45FP+45.7FP+46FP+47FP) | % | 0 | 29.73% | 29.73% | 31.32% | 32.85% | 35.22% | 37.48% | 39.68% | 41.8% | 43.86% | 48.1% | 51.98% | 55.56% | 58.87% | 61.92% | 64.73% | 67.34% | 69.76% | 72% | 74.08% | 75.99% | 77.78% | 79.42% | 80.95% | 82.35% | 83.66% | 84.87% | 85.99% | 87.03% | 87.98%
|  | Company: | Portsmouth Water |  |  | 153.15 | 153.15 | 153.6189 | 154.3206 | 152.7428 | 151.2643 | 149.6227 | 147.9679 | 145.7876 | 145.3542 | 144.8893 | 144.323 | 143.7557 | 143.2175 | 142.6584 | 142.1785 | 141.7779 | 141.3667 | 140.9948 | 140.6522 | 140.3192 | 140.0957 | 139.8416 | 139.6172 | 139.4423 | 139.2771 | 139.0915 | 138.9256 | 138.8128
|  | Resource Zone Name: | Company
|  | Resource Zone Number: | PRT 1
|  | Planning Scenario Name: | Dry Year Annual Average - benchmarking data
|  | Chosen Level of Service: | 1 in 200

## 9. FP SDB
Table 9: Final planning water supply
| Row Ref | Component | Derivation | Unit | Decimal places | 2017/18 | For info 2017-18 | For info 2018-19 | For info 2019-20 | 2020-21 | 2021-22 | 2022-23 | 2023-24 | 2024-25 | 2025-26 | 2026-27 | 2027-28 | 2028-29 | 2029-2030 | 2030-2031 | 2031-2032 | 2032-33 | 2033-34 | 2034-35 | 2035-36 | 2036-37 | 2037-38 | 2038-39 | 2039-40 | 2040-41 | 2041-42 | 2042-43 | 2043-44 | 2044-45
SDB | 11FP | Distribution Input | 19FP+20FP+21FP+22FP+32FP+33FP+38FP+39FP | Ml/d | 2 | 153.43 | 153.43 | 153.8889 | 154.6006 | 153.0128 | 151.5343 | 149.8927 | 148.2379 | 146.0576 | 145.6242 | 145.1593 | 144.593 | 144.0257 | 143.4875 | 142.9284 | 142.4485 | 142.0479 | 141.6367 | 141.2648 | 140.9222 | 140.5892 | 140.3657 | 140.1116 | 139.8872 | 139.7123 | 139.5471 | 139.3615 | 139.1956 | 139.0828
| 12FP | Water Available For Use (own sources) | 7FP-(9FP+10FP) | Ml/d | 2 | 183.84 | 183.84 | 183.84 | 191.48 | 191.4445 | 191.409 | 191.3735 | 190.888 | 203.3525 | 203.317 | 203.2815 | 203.246 | 203.2105 | 225.035 | 224.9995 | 224.964 | 224.9285 | 224.893 | 224.8575 | 224.822 | 224.7865 | 224.751 | 224.7155 | 224.68 | 224.6445 | 224.609 | 224.5735 | 224.538 | 224.5025
| 13FP | Total Water Available For Use | 12FP+(2FP+3FP)-(5FP+6FP) | Ml/d | 2 | 168.84 | 168.84 | 168.84 | 168.98 | 161.4445 | 161.409 | 161.3735 | 160.888 | 164.3525 | 164.317 | 164.2815 | 164.246 | 164.2105 | 165.035 | 164.9995 | 164.964 | 164.9285 | 164.893 | 164.8575 | 164.822 | 164.7865 | 164.751 | 164.7155 | 164.68 | 164.6445 | 164.609 | 164.5735 | 164.538 | 164.5025
| 14FP | Target headroom (climate change component) | Input | Ml/d | 2 | 1.578 | 1.6306 | 1.6832 | 1.7523 | 1.8156 | 1.785 | 1.8756 | 1.9795 | 2.128 | 1.9461 | 2.116 | 2.2878 | 2.5578 | 2.4897 | 2.2616 | 2.5605 | 2.806 | 3.0221 | 3.1584 | 2.9498 | 3.4 | 3.5853 | 3.77 | 3.9114 | 3.6828 | 3.817 | 4.0656 | 4.2294 | 4.3964
| 15FP | Target headroom (All other components) | Input | Ml/d | 2 | 3.682 | 3.6294 | 3.5768 | 3.5577 | 3.5244 | 3.315 | 3.3344 | 3.3705 | 3.472 | 3.0439 | 3.174 | 3.2922 | 3.5322 | 3.3003 | 2.8784 | 3.1295 | 3.294 | 3.4079 | 3.4216 | 3.0702 | 3.4 | 3.4447 | 3.48 | 3.4686 | 3.1372 | 3.123 | 3.1944 | 3.1906 | 3.1836
| 16FP | Target Headroom | 14FP+15FP | Ml/d | 2 | 5.26 | 5.26 | 5.26 | 5.31 | 5.34 | 5.1 | 5.21 | 5.35 | 5.6 | 4.99 | 5.29 | 5.58 | 6.09 | 5.79 | 5.14 | 5.69 | 6.1 | 6.43 | 6.58 | 6.02 | 6.8 | 7.03 | 7.25 | 7.38 | 6.82 | 6.94 | 7.26 | 7.42 | 7.58
| 17FP | Available Headroom | 13FP-11FP | Ml/d | 2 | 15.41 | 15.41 | 14.9511 | 14.3794 | 8.4317 | 9.8747 | 11.4808 | 12.6501 | 18.2949 | 18.6928 | 19.1222 | 19.653 | 20.1848 | 21.5475 | 22.0711 | 22.5155 | 22.8806 | 23.2563 | 23.5927 | 23.8998 | 24.1973 | 24.3853 | 24.6039 | 24.7928 | 24.9322 | 25.0619 | 25.212 | 25.3424 | 25.4197
| 18FP | Supply Demand Balance | 17FP-16FP | Ml/d | 2 | 10.15 | 10.15 | 9.6911 | 9.0694 | 3.0917 | 4.7747 | 6.2708 | 7.3001 | 12.6949 | 13.7028 | 13.8322 | 14.073 | 14.0948 | 15.7575 | 16.9311 | 16.8255 | 16.7806 | 16.8263 | 17.0127 | 17.8798 | 17.3973 | 17.3553 | 17.3539 | 17.4128 | 18.1122 | 18.1219 | 17.952 | 17.9224 | 17.8397
|  | Company: | Portsmouth Water
|  | Resource Zone Name: | Company
|  | Resource Zone Number: | PRT 1
|  | Planning Scenario Name: | Dry Year Annual Average - benchmarking data
|  | Chosen Level of Service: | 1 in 200

## 10. Drought plan links
Table 10: Drought plan links and Deployable Output Overview
10.1 Planning scenarios |  |  |  |  | 10.2 Water resources management plan | [7 empty] | 10.3 Drought plan | [5 empty] | 10.4 Demand
Drought Scenarios | Drought Description | Drought Severity | Plan in which scenario is used (highlights overlaps) |  | WRMP DO of Sources (not including drought measures) | WRMP Additional Yield from Drought Supply Measures (eg drought permits or orders) |  |  | WRMP Impact on DO of drought plan Demand Restrictions (eg TUBs) |  |  | WRMP DO Levels of Service | Drought Plan Additional Yield from Further Supply Measures (eg drought permits or orders) |  |  | Drought Plan Impact on DO of Further Demand Restrictions (eg TUBs) |  |  | Unrestricted Demand | Restricted Demand
|  |  | WRMP | Drought Plan | DO (Ml/d) | Description | Marginal Benefit (Ml/d) | DO (Ml/d) | Description | Marginal Benefit (Ml/d) | DO (Ml/d) | DO (Ml/d) | Description | Marginal Benefit (Ml/d) | DO (Ml/d) | Description | Marginal Benefit (Ml/d) | DO (Ml/d) | Ml/d | Ml/d
Historic Droughts | Historic | 1 in 40 (2.5%) | Y | Y | 212 | none | 0 | 0 | Hosepipe Ban | 12.6 | 0 | 0 | none | 0 | 0 | Hosepipe Ban | 12.6 | 0 | 175.3 | 162.7
| Worst Drought on Record | 1 in 50 (2.0%) | Y | Y | 210 | none | 0 | 0 | Hosepipe Ban | 12.6 | 0 | 0 | none | 0 | 0 | Hosepipe Ban | 12.6 | 0 | 175.3 | 162.7
| Extended Drought | 1 in 80 (1.25%) | Y | Y | 207 | none | 0 | 0 | Hosepipe Ban | 12.6 | 0 | 0 | none | 0 | 0 | Hosepipe Ban | 12.6 | 0 | 175.3 | 162.7
| Serious Drought | 1 in 125 (0.8%) | Y | Y | 198 | Drought Permit | 8.5 | 8.5 | Non Essential | 20.7 | 0 | 0 | Drought Permit | 8.5 | 8.5 | Nonj Essential | 20.7 | 0 | 175.3 | 154.6
Additional Drought Scenarios | Severe Drought | 1 in 200 (0.5%) | Y | Y | 191 | Drought Permit | 8.5 | 8.5 | Non Essential | 20.7 | 0 | 0 | Drought Permit | 8.5 | 8.5 | Nonj Essential | 20.7 | 0 | 175.3 | 154.6
| Extreme Drought | 1 in 500 (0.2%) | N | N | 180 | Drought Permit | 8.5 | 8.5 | Non Essential | 20.7 | 0 | 0 | Drought Permit | 8.5 | 8.5 | Nonj Essential | 20.7 | 0 | 175.3 | 154.6
Reported DO for WRMP tables highlighted in yellow
10.5 Summary report
WRMP DO Overview | [8 empty] | Drought Plan Overview
This set of Tables is for 'Severe Drought' with a return period of 1 in 200. This represents the 'Reference Level of Service' which Portsmouth Water has selected as its 'Design Drought'. The DO has been calculated using simulated weather data and there is an allowance for Climate Change. Compared to previous WRMP the DO is lower and the level of resilience is higher. | [8 empty] | The Drought Plan is directly linked to the WRMP and uses the same Scenarios. The Drought Plan is an operational plan that sets out how the demand restrictions and Drought Permits will be managed. Portsmouth Water has no raw water strorage and there is no impact of demand restrictions on DO.
Additional Drought Scenarios | [8 empty] | Drought Supply Measures and Demand Restrictions Further Details
A full range of drought scenarios has been investigated from a historic droughts, such as 1973, to the 'Severe Drought' with a return period of 1 in 200. A supply/demand balance has been produced for each scenario but only the design scenario drives investment. The WRMP does not include the 'Extreme Drought' Scenario because this is dealt with in the Emergency Plan.The additional drought scenarios are an 'Extended Drought' based on 1973 but with an extended period of low rainfall. The 'Serious Drought' which is based on lower winter rainfall and the 'Severe Drought' which is based on a four year drought with two full years without recharge.. | [8 empty] | There is only one Drought Supply Measure in the WRMP and this is the potential Drought Permit at Source S. This Drought Permit is for 8.5 Ml/d' at average and peak, and it has potential impact on the Arundel Park SSSI. Portsmouth Water will work with Southern Water to develop the monitoring plan and mitigation measures for this site. The Drought Permit is only required for a 'Serious Drought' with a return period of 1 in 125 years. Demand restrictions are brought in in phases and these are set out in the table above. The 'Historic Drought' would see calls for restraint followed by a Hosepipe Ban. As the drought developed, and a Serious Shortage of rainfall existed, then Non Essential Use Restrictions could be imposed. These restrictions would be in place for six months but this period could be extended in the most severe droughts. Each drought is different and the exact timing of restrictions will vary from drought to drought.
Impact on Supply Demand
The supply/demand balance is influenced by the scenario with deployable output falling and distribution input impacted by demand restrictions. The Dry Year represents unconstrained demands when restrictions are just avoided and DO is at its highest. The supply/demand balance is positive for the whole of the planning period for the 'Severe Drought' Scenario. This requires the 'Prefered List' of supply side and demand side options.
Demands
All of the scenarios are based on unconstained demand with no drought restrictions. As a drought develops a series of demand restrictions are introduced and DI falls to meet supply. The demand benefits shown above are cumulative and are based on simple percentage reductions. Portsmouth Water has no recent experience of drought management and the introduction of exceptions has reduced the impact of Hosepipe Bans and Non Essential Use Bans.